## Site Pass-Fail
Site Key | Site Name | Overall | Run At | Weather Condition | Rules Count | Passed | Failed | Comm Pass | Comm Fail | Perf Pass | Perf Fail
S40834 | Green Elementary | FAIL | 2026-06-08T21:55:02Z | Partly Cloudy | 23 | 20 | 3 | 1 | 0 | 1 | 0
S40835 | Gallia Academy | FAIL | 2026-06-08T06:51:25Z | Partly Cloudy | 23 | 18 | 5 | 1 | 0 | 0 | 1
S40836 | Rio Grande Elementary | FAIL | 2026-06-08T13:59:46Z | Partly Cloudy | 23 | 20 | 3 | 1 | 0 | 1 | 0
S44485 | RRH 1 & 2 | FAIL | 2026-06-08T09:42:46Z | Sunny | 22 | 18 | 4 | 1 | 0 | 1 | 0
S44566 | RIT | FAIL | 2026-06-09T00:57:17Z | Sunny | 23 | 21 | 2 | 1 | 0 | 1 | 0
S44882 | Monroe Landfill | FAIL | 2026-06-09T00:21:58Z | Sunny | 23 | 16 | 7 | 1 | 0 | 0 | 1
S51957 | WCPS - William Perry Elementary School | FAIL | 2026-06-08T20:45:58Z | Sunny | 23 | 19 | 4 | 1 | 0 | 0 | 1
S51958 | WCPS - Westwood Hills Elementary School | FAIL | 2026-06-08T21:43:06Z | Sunny | 23 | 21 | 2 | 1 | 0 | 1 | 0
S51959 | WCPS - Waynesboro High School | FAIL | 2026-06-08T16:38:57Z | Partly Cloudy | 23 | 18 | 5 | 1 | 0 | 1 | 0
S51960 | WCPS - Kate Collins Middle School | FAIL | 2026-06-08T22:21:45Z | Sunny | 23 | 18 | 5 | 1 | 0 | 1 | 0
S54553 | Butler Maple | FAIL | 2026-06-08T17:00:11Z | Partly Cloudy | 24 | 23 | 1 | 1 | 0 | 1 | 0
S54613 | Warbler | FAIL | 2026-06-08T22:14:01Z | Partly Cloudy | 23 | 21 | 2 | 1 | 0 | 0 | 1
S54681 | Eagle | FAIL | 2026-06-08T14:33:56Z | Partly Cloudy | 20 | 9 | 11 | 0 | 1 | 0 | 0
S55935 | Manuel Lawrence Dairy | FAIL | 2026-06-08T10:05:24Z | Sunny | 23 | 17 | 6 | 1 | 0 | 0 | 0
S59656 | Whitetail | FAIL | 2026-06-08T09:15:11Z | Sunny | 24 | 17 | 7 | 1 | 0 | 1 | 0
S63837 | Bulloch 1B | FAIL | 2026-06-08T08:43:29Z | Partly Cloudy | 24 | 21 | 3 | 1 | 0 | 1 | 0
S63838 | Bulloch 1A | FAIL | 2026-06-08T18:36:13Z | Sunny | 24 | 22 | 2 | 1 | 0 | 1 | 0
S63839 | Richmond | FAIL | 2026-06-09T00:58:51Z | Partly Cloudy | 24 | 18 | 6 | 1 | 0 | 1 | 0
S63840 | Upson | FAIL | 2026-06-09T03:50:49Z | Partly Cloudy | 24 | 21 | 3 | 1 | 0 | 1 | 0
S64602 | McLean | FAIL | 2026-06-08T14:32:54Z | Sunny | 24 | 16 | 8 | 1 | 0 | 1 | 0
S64603 | Shorthorn | FAIL | 2026-06-08T23:14:06Z | Sunny | 24 | 18 | 6 | 1 | 0 | 1 | 0
S65216 | Green Solar | PASS | 2026-06-08T15:57:18Z | Partly Cloudy | 24 | 24 | 0 | 1 | 0 | 1 | 0
S65784 | Washington Solar | FAIL | 2026-06-08T12:44:54Z | Sunny | 24 | 17 | 7 | 1 | 0 | 1 | 0
S65785 | Harding Solar | FAIL | 2026-05-29T06:08:36Z | Partly Cloudy | 24 | 18 | 6 | 1 | 0 | 1 | 0
S65786 | Whitehall Solar | FAIL | 2026-05-26T06:02:47Z | Partly Cloudy | 24 | 20 | 4 | 1 | 0 | 1 | 0
S65787 | Sunflower Solar | FAIL | 2026-06-08T17:31:09Z | Sunny | 24 | 19 | 5 | 1 | 0 | 1 | 0
S65788 | Gray Fox Solar | FAIL | 2026-06-01T05:58:41Z | Sunny | 24 | 17 | 7 | 1 | 0 | 0 | 1
S65918 | C & B Graham Energy | FAIL | 2026-06-08T17:47:17Z | Partly Cloudy | 21 | 8 | 13 | 0 | 1 | 0 | 0
S66000 | Auburn Solar | FAIL | 2026-06-08T18:36:02Z | Overcast | 23 | 22 | 1 | 1 | 0 | 1 | 0
S66001 | Sheridan Solar | FAIL | 2026-06-08T19:56:57Z | Partly Cloudy | 24 | 23 | 1 | 1 | 0 | 1 | 0
S66930 | Elk Solar | FAIL | 2026-06-08T08:46:08Z | Partly Cloudy | 23 | 11 | 12 | 0 | 0 | 0 | 1
S68112 | Wallace Solar | FAIL | 2026-05-26T05:56:41Z | Partly Cloudy | 24 | 22 | 2 | 1 | 0 | 1 | 0
S68113 | Marble Solar | PASS | 2026-05-24T06:34:17Z | Sunny | 24 | 24 | 0 | 1 | 0 | 1 | 0
S70532 | Longleaf Pine Solar, LLC | FAIL | 2026-06-09T03:37:29Z | Rain | 19 | 11 | 8 | 1 | 0 | 0 | 1
S70645 | Williams Solar, LLC | FAIL | 2026-06-08T08:32:26Z | Partly Cloudy | 23 | 17 | 6 | 1 | 0 | 0 | 1

## Rule Details
Site Key | Site Name | Rule Name | Type | Passed | Message | Score | Last Changed
S40834 | Green Elementary | Availability | Pass | Pass |  | 100
S40834 | Green Elementary | CheckUpload | Pass | Pass |  | 100
S40834 | Green Elementary | InverterUptime | Pass | Pass |  | 100
S40834 | Green Elementary | NetworkCom | Pass | Pass | Pass: 100.00 % PowerLogger 1000: 3 of 3 devices on port 2 communicating normally PowerLogger 1000: 11 of 11 devices on port 1 communicating normally | 100
S40834 | Green Elementary | AlertRecipients | Pass | Pass |  | 100
S40834 | Green Elementary | CheckHW | Pass | Pass |  | 100
S40834 | Green Elementary | CheckSysSize | Pass | Pass |  | 100
S40834 | Green Elementary | DefaultAlerts | Pass | Pass |  | 100
S40834 | Green Elementary | HasPVmodel | Pass | Pass |  | 100
S40834 | Green Elementary | HasWSmodel | Pass | Pass |  | 100
S40834 | Green Elementary | InvalidAlerts | Fail | Fail | Site alert ' Rule Tool Alert ' ( 126379653 ) doesn't have an active configuration. | 0 | {'index': 0, 'result': 3, 'detail': "Site alert '\t\t\t Rule Tool Alert\t' (\t\t\t 126379653\t) doesn't have an active configuration.", 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S40834 | Green Elementary | SiteConfig | Pass | Pass |  | 100
S40834 | Green Elementary | CheckMeterVoltage | Pass | Pass |  | 100
S40834 | Green Elementary | CheckWeather | Fail | Fail | Weather Station (Standard): No change in ambient temperature | 0 | {'index': 0, 'result': 3, 'detail': 'No change in ambient temperature', 'success': 0.0, 'hardwareKey': 'H119161', 'hardwareName': 'Weather Station (Standard)', 'isAcknowledged': False}
S40834 | Green Elementary | DataCuration | Fail | Fail | Weather Station (Standard): The value " Ambient temp " ( TempF ) is stuck at -20.200 °F . | 100 | {'index': 0, 'result': 3, 'detail': 'The value "\t\t\t Ambient temp\t" (\t\t\t TempF\t) is stuck at \t\t\t -20.200\t \t\t\t °F\t.', 'success': 1.0, 'hardwareKey': 'H119161', 'hardwareName': 'Weather Station (Standard)', 'isAcknowledged': False}
S40834 | Green Elementary | kWandkWh | Pass | Pass |  | 100
S40834 | Green Elementary | PVPMenergy | Pass | Pass | Elkor MKII Production Meter: Inverter / meter energy correlation: % | 97.6637
S40834 | Green Elementary | CheckPMCTs | Pass | Pass | Elkor MKII Production Meter: Phase current ratio 98.16743905668737 %, PF: 0.9967669907722094 | 98.1674
S40834 | Green Elementary | EnergyRatio | Pass | Pass |  | 76.1158
S40834 | Green Elementary | ProductionEnergy | Pass | Pass |  | 100
S40834 | Green Elementary | PVlosses | Pass | Pass |  | 100
S40834 | Green Elementary | PVmodelEnergy24 | Pass | Pass |  | 87.0831
S40834 | Green Elementary | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S40835 | Gallia Academy | Availability | Fail | Fail | Solectria 36kW Inverter - 1: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H119285', 'hardwareName': 'Solectria 36kW Inverter - 1', 'isAcknowledged': False}
S40835 | Gallia Academy | CheckUpload | Fail | Fail | Solectria 36kW Inverter - 1: Last upload: 4/6/2026 10:57 AM ( US/Eastern ), delay: 62 d 15.9 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 4/6/2026 10:57 AM\t (\t\t\t US/Eastern\t), delay: \t\t\t 62 d 15.9 h\t', 'success': 0.0, 'hardwareKey': 'H119285', 'hardwareName': 'Solectria 36kW Inverter - 1', 'isAcknowledged': False}
S40835 | Gallia Academy | InverterUptime | Fail | Fail | Fail: 0.00 % Solectria 36kW Inverter - 1: Inverter uptime: 0 % 1 of 20 inverters failed to achieve an uptime of 100 % | 0 | {'index': 0, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H119285', 'hardwareName': 'Solectria 36kW Inverter - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': '\t\t\t 1\t of \t\t\t 20\t inverters failed to achieve an uptime of \t\t\t 100\t %', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S40835 | Gallia Academy | NetworkCom | Pass | Pass | Pass: 100.00 % PowerLogger 1000: 4 of 4 devices on port 2 communicating normally PowerLogger 1000: 19 of 20 devices on port 1 communicating normally | 100
S40835 | Gallia Academy | AlertRecipients | Pass | Pass |  | 100
S40835 | Gallia Academy | CheckHW | Pass | Pass |  | 100
S40835 | Gallia Academy | CheckSysSize | Pass | Pass |  | 100
S40835 | Gallia Academy | DefaultAlerts | Pass | Pass |  | 100
S40835 | Gallia Academy | HasPVmodel | Pass | Pass |  | 100
S40835 | Gallia Academy | HasWSmodel | Pass | Pass |  | 100
S40835 | Gallia Academy | InvalidAlerts | Fail | Fail | Site alert ' Rule Tool Alert ' ( 126510797 ) doesn't have an active configuration. | 0 | {'index': 0, 'result': 3, 'detail': "Site alert '\t\t\t Rule Tool Alert\t' (\t\t\t 126510797\t) doesn't have an active configuration.", 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S40835 | Gallia Academy | SiteConfig | Pass | Pass |  | 100
S40835 | Gallia Academy | CheckMeterVoltage | Pass | Pass |  | 100
S40835 | Gallia Academy | CheckWeather | Pass | Pass |  | 100
S40835 | Gallia Academy | DataCuration | Pass | Pass |  | 100
S40835 | Gallia Academy | kWandkWh | Pass | Pass |  | 100
S40835 | Gallia Academy | PVPMenergy | Pass | Pass | Pass: 96.93 % Elkor Production Meter (Main): Adjusted inverter / meter energy correlation: %, DC capacity for offline inverters = % Elkor Production Meter (Remote): Inverter / meter energy correlation: % | 96.9308
S40835 | Gallia Academy | CheckPMCTs | Pass | Pass | Pass: 100.00 % Elkor Production Meter (Main): Phase current ratio 95.55214731233977 %, PF: 0.9988524433456007 Elkor Production Meter (Remote): Phase current ratio 97.33317381430035 %, PF: 0.997869937463768 | 100
S40835 | Gallia Academy | EnergyRatio | Pass | Pass |  | 73.2281
S40835 | Gallia Academy | ProductionEnergy | Pass | Pass |  | 100
S40835 | Gallia Academy | PVlosses | Fail | Fail | Fail: 0.00 % Solectria 36kW Inverter - 1: Downtime loss detected: 99.83897621189234 % ( 227.69043799999992 kWh) Solectria 36kW Inverter - 12: Excessive residual loss: 28.753059132461438 % Elkor Production Meter (Main): Excessive soiling loss: 5.27551 % ( 123.71066881611713 kWh) | 0 | {'index': 0, 'result': 3, 'detail': 'Downtime loss detected: \t\t\t 99.83897621189234\t % (\t\t\t 227.69043799999992\t kWh)', 'success': 0.0, 'hardwareKey': 'H119285', 'hardwareName': 'Solectria 36kW Inverter - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t 28.753059132461438\t %', 'success': 0.0, 'hardwareKey': 'H119296', 'hardwareName': 'Solectria 36kW Inverter - 12', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 5.27551\t % (\t\t\t 123.71066881611713\t kWh)', 'success': 0.0, 'hardwareKey': 'H119267', 'hardwareName': 'Elkor Production Meter (Main)', 'isAcknowledged': False}
S40835 | Gallia Academy | PVmodelEnergy24 | Pass | Pass |  | 94.7574
S40835 | Gallia Academy | CorrectiveAction | Pass | Pass | Slight losses or device availability issues should be addressed during the next scheduled maintenance activity. | 95
S40836 | Rio Grande Elementary | Availability | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | CheckUpload | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | InverterUptime | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | NetworkCom | Pass | Pass | Pass: 100.00 % PowerLogger 1000: 3 of 3 devices on port 2 communicating normally PowerLogger 1000: 13 of 13 devices on port 1 communicating normally | 100
S40836 | Rio Grande Elementary | AlertRecipients | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | CheckHW | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | CheckSysSize | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | DefaultAlerts | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | HasPVmodel | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | HasWSmodel | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | InvalidAlerts | Fail | Fail | Site alert ' Rule Tool Alert ' ( 126450830 ) doesn't have an active configuration. | 0 | {'index': 0, 'result': 3, 'detail': "Site alert '\t\t\t Rule Tool Alert\t' (\t\t\t 126450830\t) doesn't have an active configuration.", 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S40836 | Rio Grande Elementary | SiteConfig | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | CheckMeterVoltage | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | CheckWeather | Fail | Fail | Weather Station 2 (GHI) (SO31651): No change in module temperature, sensor # | 0 | {'index': 0, 'result': 3, 'detail': 'No change in module temperature, sensor #', 'success': 0.0, 'hardwareKey': 'H259072', 'hardwareName': 'Weather Station 2 (GHI) (SO31651)', 'isAcknowledged': False}
S40836 | Rio Grande Elementary | DataCuration | Fail | Fail | Weather Station 2 (GHI) (SO31651): The value " Module temp " ( Temp1 ) is stuck at -40 °F . | 100 | {'index': 0, 'result': 3, 'detail': 'The value "\t\t\t Module temp\t" (\t\t\t Temp1\t) is stuck at \t\t\t -40\t \t\t\t °F\t.', 'success': 1.0, 'hardwareKey': 'H259072', 'hardwareName': 'Weather Station 2 (GHI) (SO31651)', 'isAcknowledged': False}
S40836 | Rio Grande Elementary | kWandkWh | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | PVPMenergy | Pass | Pass | Elkor Production Meter: Inverter / meter energy correlation: % | 96.569
S40836 | Rio Grande Elementary | CheckPMCTs | Pass | Pass | Elkor Production Meter: Phase current ratio 97.63946944148998 %, PF: 0.9964612793097424 | 97.6395
S40836 | Rio Grande Elementary | EnergyRatio | Pass | Pass |  | 77.0758
S40836 | Rio Grande Elementary | ProductionEnergy | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | PVlosses | Pass | Pass |  | 100
S40836 | Rio Grande Elementary | PVmodelEnergy24 | Pass | Pass |  | 88.7984
S40836 | Rio Grande Elementary | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S44485 | RRH 1 & 2 | Availability | Fail | Fail | KYZ Pulse Meter: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H154309', 'hardwareName': 'KYZ Pulse Meter', 'isAcknowledged': False}
S44485 | RRH 1 & 2 | CheckUpload | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | InverterUptime | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | NetworkCom | Pass | Pass | Pass: 100.00 % PowerLogger 1000 Site 1 - 1: 16 of 16 devices on port 1 communicating normally PowerLogger 1000 Site 1 - 2: 4 of 4 devices on port 2 communicating normally PowerLogger 1000 Site 1 - 2: 17 of 17 devices on port 1 communicating normally PowerLogger 1000 Site 2: 1 of 1 TCP devices communicating normally PowerLogger 1000 Site 2: 16 of 16 devices on port 1 communicating normally PowerLogger 1000 Site 2: 18 of 18 devices on port 2 communicating normally | 100
S44485 | RRH 1 & 2 | AlertRecipients | Fail | Fail | Alert email notifications disabled | 0 | {'index': 0, 'result': 3, 'detail': 'Alert email notifications disabled', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S44485 | RRH 1 & 2 | CheckHW | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | CheckSysSize | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | DefaultAlerts | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | HasPVmodel | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | HasWSmodel | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | InvalidAlerts | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | SiteConfig | Fail | Fail | Fail: 0.00 % Site hardware summary not initialized Site configured to not generate alert emails | 0 | {'index': 0, 'result': 3, 'detail': 'Site hardware summary not initialized', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Site configured to not generate alert emails', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S44485 | RRH 1 & 2 | CheckWeather | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | DataCuration | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | kWandkWh | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | PVPMenergy | Pass | Pass | Pass: 99.92 % Elkor Production Meter Site 1: Inverter / meter energy correlation: % Elkor Production Meter Site 2: Inverter / meter energy correlation: % | 99.9211
S44485 | RRH 1 & 2 | CheckPMCTs | Pass | Pass | Pass: 100.00 % Elkor Production Meter Site 1: Phase current ratio 96.75423779829251 %, PF: 0.9994653025799644 Elkor Production Meter Site 2: Phase current ratio 95.1885220595177 %, PF: 0.999452670025103 | 100
S44485 | RRH 1 & 2 | EnergyRatio | Pass | Pass |  | 93.1598
S44485 | RRH 1 & 2 | ProductionEnergy | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | PVlosses | Pass | Pass |  | 100
S44485 | RRH 1 & 2 | PVmodelEnergy24 | Pass | Pass |  | 103.2037
S44485 | RRH 1 & 2 | CorrectiveAction | Fail | Fail | Equipment repair required. Low availability , Extra meter : KYZ Pulse Meter | 50 | {'index': 0, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Low availability\t, \t\t\t Extra meter\t: \t\t\t KYZ Pulse Meter\t', 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S44566 | RIT | Availability | Pass | Pass |  | 100
S44566 | RIT | CheckUpload | Pass | Pass |  | 100
S44566 | RIT | InverterUptime | Pass | Pass |  | 100
S44566 | RIT | NetworkCom | Pass | Pass | Pass: 100.00 % PowerLogger1000 - 1: 12 of 12 devices on port 1 communicating normally PowerLogger1000 - 1: 8 of 8 devices on port 2 communicating normally PowerLogger1000 - 2: 4 of 4 devices on port 2 communicating normally PowerLogger1000 - 2: 7 of 7 devices on port 1 communicating normally | 100
S44566 | RIT | AlertRecipients | Pass | Pass |  | 100
S44566 | RIT | CheckHW | Fail | Fail | Fail: 0.00 % Elkor Production Meter: Production meter capacity is not equal to the sum of the connected inverters. Meter: kW, Inverters: kW Chint SCA60KTL Inverter - 1: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 2: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 3: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 4: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 5: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 6: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 7: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 8: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 9: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 10: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 11: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 12: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 13: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 14: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 15: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 16: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 17: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 18: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 19: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 20: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 21: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 22: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 23: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 24: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 25: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 26: Low diffuse shade factor on (should be greater than 0.5) Chint SCA60KTL Inverter - 27: Low diffuse shade factor on (should be greater than 0.5) | 0 | {'index': 0, 'result': 3, 'detail': 'Production meter capacity is not equal to the sum of the connected inverters. Meter: kW, Inverters: kW', 'success': 0.0, 'hardwareKey': 'H143477', 'hardwareName': 'Elkor Production Meter', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Low diffuse shade factor on (should be greater than 0.5)', 'success': 0.0, 'hardwareKey': 'H143483', 'hardwareName': 'Chint SCA60KTL Inverter - 1', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Low diffuse shade factor on (should be greater than 0.5)', 'success': 0.0, 'hardwareKey': 'H143484', 'hardwareName': 'Chint SCA60KTL Inverter - 2', 'isAcknowledged': False}
S44566 | RIT | CheckSysSize | Pass | Pass |  | 100
S44566 | RIT | DefaultAlerts | Pass | Pass |  | 100
S44566 | RIT | HasPVmodel | Pass | Pass |  | 100
S44566 | RIT | HasWSmodel | Pass | Pass |  | 100
S44566 | RIT | InvalidAlerts | Pass | Pass |  | 100
S44566 | RIT | SiteConfig | Pass | Pass |  | 100
S44566 | RIT | CheckMeterVoltage | Pass | Pass |  | 100
S44566 | RIT | CheckWeather | Pass | Pass |  | 100
S44566 | RIT | DataCuration | Pass | Pass |  | 100
S44566 | RIT | kWandkWh | Pass | Pass |  | 100
S44566 | RIT | PVPMenergy | Pass | Pass | Elkor Production Meter: Inverter / meter energy correlation: % | 98.8454
S44566 | RIT | CheckPMCTs | Pass | Pass | Elkor Production Meter: Phase current ratio 98.78524589008428 %, PF: 0.9939369230430933 | 98.7852
S44566 | RIT | EnergyRatio | Fail | Fail | Fail: 0.00 % Chint SCA60KTL Inverter - 1: High energy ratio: 1.161069073364561 Chint SCA60KTL Inverter - 2: High energy ratio: 1.2153759682211795 Chint SCA60KTL Inverter - 3: High energy ratio: 1.1583050881483714 Chint SCA60KTL Inverter - 4: High energy ratio: 1.1606803553619474 Chint SCA60KTL Inverter - 6: High energy ratio: 1.1583212489491592 Chint SCA60KTL Inverter - 8: High energy ratio: 1.158184590816296 | 0 | {'index': 0, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.161069073364561\t', 'success': 0.0, 'hardwareKey': 'H143483', 'hardwareName': 'Chint SCA60KTL Inverter - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.2153759682211795\t', 'success': 0.0, 'hardwareKey': 'H143484', 'hardwareName': 'Chint SCA60KTL Inverter - 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.1583050881483714\t', 'success': 0.0, 'hardwareKey': 'H143485', 'hardwareName': 'Chint SCA60KTL Inverter - 3', 'isAcknowledged': False}
S44566 | RIT | ProductionEnergy | Pass | Pass |  | 100
S44566 | RIT | PVlosses | Pass | Pass |  | 100
S44566 | RIT | PVmodelEnergy24 | Pass | Pass |  | 106.9527
S44566 | RIT | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S44882 | Monroe Landfill | Availability | Fail | Fail | Solectria PVI 60KTL Inverter - 20: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H155958', 'hardwareName': 'Solectria PVI 60KTL Inverter - 20', 'isAcknowledged': False}
S44882 | Monroe Landfill | CheckUpload | Pass | Pass |  | 100
S44882 | Monroe Landfill | InverterUptime | Fail | Fail | Fail: 0.00 % Solectria PVI 60KTL Inverter - 20: Inverter uptime: 0 % 1 of 27 inverters failed to achieve an uptime of 100 % | 0 | {'index': 0, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H155958', 'hardwareName': 'Solectria PVI 60KTL Inverter - 20', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': '\t\t\t 1\t of \t\t\t 27\t inverters failed to achieve an uptime of \t\t\t 100\t %', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S44882 | Monroe Landfill | NetworkCom | Pass | Pass | Pass: 100.00 % PowerLogger1000 - 1: 12 of 12 devices on port 1 communicating normally PowerLogger1000 - 2: 2 of 2 devices on port 2 communicating normally PowerLogger1000 - 2: 15 of 15 devices on port 1 communicating normally | 100
S44882 | Monroe Landfill | AlertRecipients | Pass | Pass |  | 100
S44882 | Monroe Landfill | CheckHW | Pass | Pass |  | 100
S44882 | Monroe Landfill | CheckSysSize | Pass | Pass |  | 100
S44882 | Monroe Landfill | DefaultAlerts | Fail | Fail | Elkor Production Meter: Default alerts not set: 350 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 350\t', 'success': 0.0, 'hardwareKey': 'H155936', 'hardwareName': 'Elkor Production Meter', 'isAcknowledged': False}
S44882 | Monroe Landfill | HasPVmodel | Pass | Pass |  | 100
S44882 | Monroe Landfill | HasWSmodel | Pass | Pass |  | 100
S44882 | Monroe Landfill | InvalidAlerts | Pass | Pass |  | 100
S44882 | Monroe Landfill | SiteConfig | Pass | Pass |  | 100
S44882 | Monroe Landfill | CheckMeterVoltage | Pass | Pass |  | 100
S44882 | Monroe Landfill | CheckWeather | Pass | Pass |  | 100
S44882 | Monroe Landfill | DataCuration | Fail | Fail | Fail: 0.00 % Solectria PVI 60KTL Inverter - 20: The value " AC Power Output " ( KwAC ) is stuck at 0 kW . Solectria PVI 60KTL Inverter - 20: The value " Phase A Current " ( IacA ) is stuck at 0 A . Solectria PVI 60KTL Inverter - 20: The value " Phase B Current " ( IacB ) is stuck at 0 A . Solectria PVI 60KTL Inverter - 20: The value " Phase C Current " ( IacC ) is stuck at 0 A . | 0 | {'index': 0, 'result': 3, 'detail': 'The value "\t\t\t AC Power Output\t" (\t\t\t KwAC\t) is stuck at \t\t\t 0\t \t\t\t kW\t.', 'success': 0.0, 'hardwareKey': 'H155958', 'hardwareName': 'Solectria PVI 60KTL Inverter - 20', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'The value "\t\t\t Phase A Current\t" (\t\t\t IacA\t) is stuck at \t\t\t 0\t \t\t\t A\t.', 'success': 0.0, 'hardwareKey': 'H155958', 'hardwareName': 'Solectria PVI 60KTL Inverter - 20', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'The value "\t\t\t Phase B Current\t" (\t\t\t IacB\t) is stuck at \t\t\t 0\t \t\t\t A\t.', 'success': 0.0, 'hardwareKey': 'H155958', 'hardwareName': 'Solectria PVI 60KTL Inverter - 20', 'isAcknowledged': False}
S44882 | Monroe Landfill | kWandkWh | Pass | Pass |  | 100
S44882 | Monroe Landfill | PVPMenergy | Pass | Pass | Elkor Production Meter: Inverter / meter energy correlation: % | 99.4238
S44882 | Monroe Landfill | CheckPMCTs | Pass | Pass | Elkor Production Meter: Phase current ratio 97.4646032268686 %, PF: 0.9994117397888141 | 97.4646
S44882 | Monroe Landfill | EnergyRatio | Fail | Fail | Fail: 0.00 % Solectria PVI 60KTL Inverter - 1: High energy ratio: 1.2408658892274098 Solectria PVI 60KTL Inverter - 2: High energy ratio: 1.292035616618231 Solectria PVI 60KTL Inverter - 3: High energy ratio: 1.2613337801837383 Solectria PVI 60KTL Inverter - 4: High energy ratio: 1.2715677256619025 Solectria PVI 60KTL Inverter - 5: High energy ratio: 1.2587752938140482 Solectria PVI 60KTL Inverter - 6: High energy ratio: 1.2664507529228204 Solectria PVI 60KTL Inverter - 7: High energy ratio: 1.2818016711400666 Solectria PVI 60KTL Inverter - 8: High energy ratio: 1.2945941029877719 Solectria PVI 60KTL Inverter - 9: High energy ratio: 1.18969616183644 Solectria PVI 60KTL Inverter - 10: High energy ratio: 1.2843601575097567 Solectria PVI 60KTL Inverter - 11: High energy ratio: 1.2843601575096077 Solectria PVI 60KTL Inverter - 12: High energy ratio: 1.304828048466085 Solectria PVI 60KTL Inverter - 13: High energy ratio: 1.2861258734548071 Solectria PVI 60KTL Inverter - 14: High energy ratio: 1.3073865348354772 Solectria PVI 60KTL Inverter - 15: High energy ratio: 1.2664507529229694 Solectria PVI 60KTL Inverter - 16: High energy ratio: 1.2741262120315924 Solectria PVI 60KTL Inverter - 17: High energy ratio: 1.2843601575096077 Solectria PVI 60KTL Inverter - 18: High energy ratio: 1.199930107314753 Solectria PVI 60KTL Inverter - 19: High energy ratio: 1.3091243746336392 Solectria PVI 60KTL Inverter - 21: High energy ratio: 1.302269562096395 Solectria PVI 60KTL Inverter - 22: High energy ratio: 1.207605566423525 Solectria PVI 60KTL Inverter - 23: High energy ratio: 1.297152589357313 Solectria PVI 60KTL Inverter - 24: High energy ratio: 1.253658321075115 Solectria PVI 60KTL Inverter - 25: High energy ratio: 1.2843601575096077 Solectria PVI 60KTL Inverter - 26: High energy ratio: 1.2988502765744891 Solectria PVI 60KTL Inverter - 27: High energy ratio: 1.2945941029877719 Elkor Production Meter: High energy ratio: 1.2193556519723794 | 0 | {'index': 0, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.2408658892274098\t', 'success': 0.0, 'hardwareKey': 'H155939', 'hardwareName': 'Solectria PVI 60KTL Inverter - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.292035616618231\t', 'success': 0.0, 'hardwareKey': 'H155940', 'hardwareName': 'Solectria PVI 60KTL Inverter - 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.2613337801837383\t', 'success': 0.0, 'hardwareKey': 'H155941', 'hardwareName': 'Solectria PVI 60KTL Inverter - 3', 'isAcknowledged': False}
S44882 | Monroe Landfill | ProductionEnergy | Pass | Pass |  | 100
S44882 | Monroe Landfill | PVlosses | Fail | Fail | Fail: 0.00 % Solectria PVI 60KTL Inverter - 2: Excessive residual loss: -29.983261425510428 % Solectria PVI 60KTL Inverter - 3: Excessive residual loss: -26.678816982178216 % Solectria PVI 60KTL Inverter - 4: Excessive residual loss: -27.543032704779787 % Solectria PVI 60KTL Inverter - 5: Excessive residual loss: -26.308882581474236 % Solectria PVI 60KTL Inverter - 6: Excessive residual loss: -27.277119646811286 % Solectria PVI 60KTL Inverter - 7: Excessive residual loss: -29.060270604408572 % Solectria PVI 60KTL Inverter - 8: Excessive residual loss: -29.88038793550123 % Solectria PVI 60KTL Inverter - 10: Excessive residual loss: -28.53790340942045 % Solectria PVI 60KTL Inverter - 11: Excessive residual loss: -29.01987149876664 % Solectria PVI 60KTL Inverter - 12: Excessive residual loss: -31.19148230304562 % Solectria PVI 60KTL Inverter - 13: Excessive residual loss: -29.169191838597357 % Solectria PVI 60KTL Inverter - 14: Excessive residual loss: -31.704960668911607 % Solectria PVI 60KTL Inverter - 15: Excessive residual loss: -27.38547311799452 % Solectria PVI 60KTL Inverter - 16: Excessive residual loss: -28.126549748559544 % Solectria PVI 60KTL Inverter - 17: Excessive residual loss: -29.249537077992983 % Solectria PVI 60KTL Inverter - 19: Excessive residual loss: -31.4467616390621 % Solectria PVI 60KTL Inverter - 20: Downtime loss detected: 99.62318600262489 % ( 389.99333549999994 kWh) Solectria PVI 60KTL Inverter - 21: Excessive residual loss: -30.39706892835074 % Solectria PVI 60KTL Inverter - 23: Excessive residual loss: -29.91894571903364 % Solectria PVI 60KTL Inverter - 24: Excessive residual loss: -26.08397389474188 % Solectria PVI 60KTL Inverter - 25: Excessive residual loss: -28.642274886636304 % Solectria PVI 60KTL Inverter - 26: Excessive residual loss: -30.30688276240013 % Solectria PVI 60KTL Inverter - 27: Excessive residual loss: -29.923768535615352 % | 0 | {'index': 0, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t -29.983261425510428\t %', 'success': 0.0, 'hardwareKey': 'H155940', 'hardwareName': 'Solectria PVI 60KTL Inverter - 2', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t -26.678816982178216\t %', 'success': 0.0, 'hardwareKey': 'H155941', 'hardwareName': 'Solectria PVI 60KTL Inverter - 3', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t -27.543032704779787\t %', 'success': 0.0, 'hardwareKey': 'H155942', 'hardwareName': 'Solectria PVI 60KTL Inverter - 4', 'isAcknowledged': False}
S44882 | Monroe Landfill | PVmodelEnergy24 | Fail | Fail | Energy above expected ( 121.9355705654503 %) | 121.9356 | {'index': 0, 'result': 3, 'detail': 'Energy above expected (\t\t\t 121.9355705654503\t %)', 'success': 1.219355705654503, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S44882 | Monroe Landfill | CorrectiveAction | Pass | Pass | Slight losses or device availability issues should be addressed during the next scheduled maintenance activity. | 95
S51957 | WCPS - William Perry Elementary School | Availability | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | CheckUpload | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | InverterUptime | Fail | Fail | Fail: 0.00 % CPS SCA60KTL Inverter - 1: Inverter uptime: 93.2203389830509 % 1 of 3 inverters failed to achieve an uptime of 100 % | 0 | {'index': 0, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 93.2203389830509\t %', 'success': 0.0, 'hardwareKey': 'H226501', 'hardwareName': 'CPS SCA60KTL Inverter - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': '\t\t\t 1\t of \t\t\t 3\t inverters failed to achieve an uptime of \t\t\t 100\t %', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S51957 | WCPS - William Perry Elementary School | NetworkCom | Pass | Pass | Pass: 100.00 % PLCS400 Logger (RMA16004 SO100553): 2 of 2 devices on port 2 communicating normally PLCS400 Logger (RMA16004 SO100553): 3 of 3 devices on port 1 communicating normally | 100
S51957 | WCPS - William Perry Elementary School | AlertRecipients | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | CheckHW | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | CheckSysSize | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | DefaultAlerts | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | HasPVmodel | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | HasWSmodel | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | InvalidAlerts | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | SiteConfig | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | CheckMeterVoltage | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | CheckWeather | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | DataCuration | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | kWandkWh | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | PVPMenergy | Pass | Pass | AcuRev Production Meter: Inverter / meter energy correlation: % | 99.4648
S51957 | WCPS - William Perry Elementary School | CheckPMCTs | Pass | Pass | AcuRev Production Meter: Phase current ratio 99.04501082043157 %, PF: 0.998958815622717 | 99.045
S51957 | WCPS - William Perry Elementary School | EnergyRatio | Fail | Fail | Fail: 0.00 % CPS SCA60KTL Inverter - 1: Low energy ratio: 0.49134283833021897 CPS SCA60KTL Inverter - 2: Low energy ratio: 0.4452724910224106 CPS SCA60KTL Inverter - 3: Low energy ratio: 0.4722442660397089 AcuRev Production Meter: Low energy ratio: 0.4721553282941796 | 0 | {'index': 0, 'result': 3, 'detail': 'Low energy ratio: \t\t\t 0.49134283833021897\t', 'success': 0.0, 'hardwareKey': 'H226501', 'hardwareName': 'CPS SCA60KTL Inverter - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Low energy ratio: \t\t\t 0.4452724910224106\t', 'success': 0.0, 'hardwareKey': 'H226502', 'hardwareName': 'CPS SCA60KTL Inverter - 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Low energy ratio: \t\t\t 0.4722442660397089\t', 'success': 0.0, 'hardwareKey': 'H226503', 'hardwareName': 'CPS SCA60KTL Inverter - 3', 'isAcknowledged': False}
S51957 | WCPS - William Perry Elementary School | ProductionEnergy | Pass | Pass |  | 100
S51957 | WCPS - William Perry Elementary School | PVlosses | Fail | Fail | Fail: 0.00 % CPS SCA60KTL Inverter - 1: Excessive residual loss: 50.1452670004859 % CPS SCA60KTL Inverter - 2: Excessive residual loss: 51.57073288594476 % CPS SCA60KTL Inverter - 3: Excessive residual loss: 48.59383692383666 % | 0 | {'index': 0, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t 50.1452670004859\t %', 'success': 0.0, 'hardwareKey': 'H226501', 'hardwareName': 'CPS SCA60KTL Inverter - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t 51.57073288594476\t %', 'success': 0.0, 'hardwareKey': 'H226502', 'hardwareName': 'CPS SCA60KTL Inverter - 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t 48.59383692383666\t %', 'success': 0.0, 'hardwareKey': 'H226503', 'hardwareName': 'CPS SCA60KTL Inverter - 3', 'isAcknowledged': False}
S51957 | WCPS - William Perry Elementary School | PVmodelEnergy24 | Fail | Fail | Energy below expected ( 47.21553299205142 %) | 47.2155 | {'index': 0, 'result': 3, 'detail': 'Energy below expected (\t\t\t 47.21553299205142\t %)', 'success': 0.47215532992051423, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S51957 | WCPS - William Perry Elementary School | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S51958 | WCPS - Westwood Hills Elementary School | Availability | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | CheckUpload | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | InverterUptime | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | NetworkCom | Pass | Pass | Pass: 100.00 % PLCS400 Logger: 2 of 2 devices on port 2 communicating normally PLCS400 Logger: 3 of 3 devices on port 1 communicating normally | 100
S51958 | WCPS - Westwood Hills Elementary School | AlertRecipients | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | CheckHW | Fail | Fail | Microhard Modem: Alerts not set on | 0 | {'index': 0, 'result': 3, 'detail': 'Alerts not set on ', 'success': 0.0, 'hardwareKey': 'H226491', 'hardwareName': 'Microhard Modem', 'isAcknowledged': False}
S51958 | WCPS - Westwood Hills Elementary School | CheckSysSize | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | DefaultAlerts | Fail | Fail | Microhard Modem: Default alerts not set: 344 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 344\t', 'success': 0.0, 'hardwareKey': 'H226491', 'hardwareName': 'Microhard Modem', 'isAcknowledged': False}
S51958 | WCPS - Westwood Hills Elementary School | HasPVmodel | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | HasWSmodel | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | InvalidAlerts | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | SiteConfig | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | CheckMeterVoltage | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | CheckWeather | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | DataCuration | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | kWandkWh | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | PVPMenergy | Pass | Pass | AcuRev Production Meter: Inverter / meter energy correlation: % | 99.3723
S51958 | WCPS - Westwood Hills Elementary School | CheckPMCTs | Pass | Pass | AcuRev Production Meter: Phase current ratio 98.99580065793423 %, PF: 0.9969694256969085 | 98.9958
S51958 | WCPS - Westwood Hills Elementary School | EnergyRatio | Pass | Pass |  | 82.4115
S51958 | WCPS - Westwood Hills Elementary School | ProductionEnergy | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | PVlosses | Pass | Pass |  | 100
S51958 | WCPS - Westwood Hills Elementary School | PVmodelEnergy24 | Pass | Pass |  | 90.2482
S51958 | WCPS - Westwood Hills Elementary School | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S51959 | WCPS - Waynesboro High School | Availability | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | CheckUpload | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | InverterUptime | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | NetworkCom | Pass | Pass | Pass: 100.00 % PLCS400 Logger: 2 of 2 devices on port 2 communicating normally PLCS400 Logger: 2 of 2 devices on port 1 communicating normally | 100
S51959 | WCPS - Waynesboro High School | AlertRecipients | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | CheckHW | Fail | Fail | Fail: 0.00 % Microhard Modem: Alerts not set on AcuRev Production Meter: Production meter capacity is not equal to the sum of the connected inverters. Meter: kW, Inverters: kW | 0 | {'index': 0, 'result': 3, 'detail': 'Alerts not set on ', 'success': 0.0, 'hardwareKey': 'H226505', 'hardwareName': 'Microhard Modem', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Production meter capacity is not equal to the sum of the connected inverters. Meter: kW, Inverters: kW', 'success': 0.0, 'hardwareKey': 'H226507', 'hardwareName': 'AcuRev Production Meter', 'isAcknowledged': False}
S51959 | WCPS - Waynesboro High School | CheckSysSize | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | DefaultAlerts | Fail | Fail | Microhard Modem: Default alerts not set: 344 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 344\t', 'success': 0.0, 'hardwareKey': 'H226505', 'hardwareName': 'Microhard Modem', 'isAcknowledged': False}
S51959 | WCPS - Waynesboro High School | HasPVmodel | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | HasWSmodel | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | InvalidAlerts | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | SiteConfig | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | CheckMeterVoltage | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | CheckWeather | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | DataCuration | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | kWandkWh | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | PVPMenergy | Pass | Pass | AcuRev Production Meter: Inverter / meter energy correlation: % | 99.9507
S51959 | WCPS - Waynesboro High School | CheckPMCTs | Pass | Pass | AcuRev Production Meter: Phase current ratio 98.55232941380501 %, PF: 0.99746948703043 | 98.5523
S51959 | WCPS - Waynesboro High School | EnergyRatio | Fail | Fail | Fail: 0.00 % CPS SCA60KTL Inverter - 1: High energy ratio: 1.1098792585919801 CPS SCA50KTL Inverter - 2: High energy ratio: 1.1857719892597742 | 0 | {'index': 0, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.1098792585919801\t', 'success': 0.0, 'hardwareKey': 'H226508', 'hardwareName': 'CPS SCA60KTL Inverter - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.1857719892597742\t', 'success': 0.0, 'hardwareKey': 'H226509', 'hardwareName': 'CPS SCA50KTL Inverter - 2', 'isAcknowledged': False}
S51959 | WCPS - Waynesboro High School | ProductionEnergy | Pass | Pass |  | 100
S51959 | WCPS - Waynesboro High School | PVlosses | Fail | Fail | CPS SCA50KTL Inverter - 2: Excessive residual loss: -25.833508454433673 % | 0 | {'index': 0, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t -25.833508454433673\t %', 'success': 0.0, 'hardwareKey': 'H226509', 'hardwareName': 'CPS SCA50KTL Inverter - 2', 'isAcknowledged': False}
S51959 | WCPS - Waynesboro High School | PVmodelEnergy24 | Fail | Fail | Energy below expected ( 74.01138451460963 %) | 74.0114 | {'index': 0, 'result': 3, 'detail': 'Energy below expected (\t\t\t 74.01138451460963\t %)', 'success': 0.7401138451460963, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S51959 | WCPS - Waynesboro High School | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S51960 | WCPS - Kate Collins Middle School | Availability | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | CheckUpload | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | InverterUptime | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | NetworkCom | Pass | Pass | Pass: 100.00 % PLCS400 Logger: 2 of 2 devices on port 2 communicating normally PLCS400 Logger: 5 of 5 devices on port 1 communicating normally | 100
S51960 | WCPS - Kate Collins Middle School | AlertRecipients | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | CheckHW | Fail | Fail | Microhard Modem: Alerts not set on | 0 | {'index': 0, 'result': 3, 'detail': 'Alerts not set on ', 'success': 0.0, 'hardwareKey': 'H226515', 'hardwareName': 'Microhard Modem', 'isAcknowledged': False}
S51960 | WCPS - Kate Collins Middle School | CheckSysSize | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | DefaultAlerts | Fail | Fail | Microhard Modem: Default alerts not set: 344 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 344\t', 'success': 0.0, 'hardwareKey': 'H226515', 'hardwareName': 'Microhard Modem', 'isAcknowledged': False}
S51960 | WCPS - Kate Collins Middle School | HasPVmodel | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | HasWSmodel | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | InvalidAlerts | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | SiteConfig | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | CheckMeterVoltage | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | CheckWeather | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | DataCuration | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | kWandkWh | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | PVPMenergy | Pass | Pass | AcuRev Production Meter: Inverter / meter energy correlation: % | 99.7164
S51960 | WCPS - Kate Collins Middle School | CheckPMCTs | Pass | Pass | AcuRev Production Meter: Phase current ratio 99.69143907952218 %, PF: 0.9994430438565858 | 99.6914
S51960 | WCPS - Kate Collins Middle School | EnergyRatio | Fail | Fail | Fail: 0.00 % CPS SCA60KTL Inverter - 2: Low energy ratio: 0.6910718772360964 CPS SCA60KTL Inverter - 3: Low energy ratio: 0.6461587270465415 | 0 | {'index': 0, 'result': 3, 'detail': 'Low energy ratio: \t\t\t 0.6910718772360964\t', 'success': 0.0, 'hardwareKey': 'H226527', 'hardwareName': 'CPS SCA60KTL Inverter - 2', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Low energy ratio: \t\t\t 0.6461587270465415\t', 'success': 0.0, 'hardwareKey': 'H226528', 'hardwareName': 'CPS SCA60KTL Inverter - 3', 'isAcknowledged': False}
S51960 | WCPS - Kate Collins Middle School | ProductionEnergy | Pass | Pass |  | 100
S51960 | WCPS - Kate Collins Middle School | PVlosses | Fail | Fail | Fail: 0.00 % CPS SCA60KTL Inverter - 2: Excessive residual loss: 28.66594597069033 % CPS SCA60KTL Inverter - 3: Excessive residual loss: 33.061322534542796 % | 0 | {'index': 0, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t 28.66594597069033\t %', 'success': 0.0, 'hardwareKey': 'H226527', 'hardwareName': 'CPS SCA60KTL Inverter - 2', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t 33.061322534542796\t %', 'success': 0.0, 'hardwareKey': 'H226528', 'hardwareName': 'CPS SCA60KTL Inverter - 3', 'isAcknowledged': False}
S51960 | WCPS - Kate Collins Middle School | PVmodelEnergy24 | Fail | Fail | Energy below expected ( 78.40526038391509 %) | 78.4053 | {'index': 0, 'result': 3, 'detail': 'Energy below expected (\t\t\t 78.40526038391509\t %)', 'success': 0.784052603839151, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S51960 | WCPS - Kate Collins Middle School | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S54553 | Butler Maple | Availability | Pass | Pass |  | 100
S54553 | Butler Maple | CheckUpload | Pass | Pass |  | 100
S54553 | Butler Maple | InverterUptime | Pass | Pass |  | 100
S54553 | Butler Maple | NetworkCom | Pass | Pass | PowerManager 2200: 10 of 10 TCP devices communicating normally | 100
S54553 | Butler Maple | AlertRecipients | Pass | Pass |  | 100
S54553 | Butler Maple | CheckHW | Pass | Pass |  | 100
S54553 | Butler Maple | CheckSysSize | Pass | Pass |  | 100
S54553 | Butler Maple | DefaultAlerts | Fail | Fail | SEL-351 Relay: Default alerts not enabled: Device communication (250),SEL 351 Breaker Bit Alert (720) | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not enabled: \t\t\t Device communication (250),SEL 351 Breaker Bit Alert (720)\t', 'success': 0.0, 'hardwareKey': 'H262724', 'hardwareName': 'SEL-351 Relay', 'isAcknowledged': False}
S54553 | Butler Maple | HasPVmodel | Pass | Pass |  | 100
S54553 | Butler Maple | HasWSmodel | Pass | Pass |  | 100
S54553 | Butler Maple | InvalidAlerts | Pass | Pass |  | 100
S54553 | Butler Maple | SiteConfig | Pass | Pass |  | 100
S54553 | Butler Maple | CheckMeterVoltage | Pass | Pass |  | 100
S54553 | Butler Maple | CheckWeather | Pass | Pass |  | 100
S54553 | Butler Maple | DataCuration | Pass | Pass |  | 100
S54553 | Butler Maple | kWandkWh | Pass | Pass |  | 100
S54553 | Butler Maple | PVPMenergy | Pass | Pass | Schneider PM5563 Production Meter: Inverter / meter energy correlation: % | 98.4525
S54553 | Butler Maple | Tracker | Pass | Pass |  | 100
S54553 | Butler Maple | CheckPMCTs | Pass | Pass | Schneider PM5563 Production Meter: Phase current ratio 99.78556139176075 %, PF: 0.9963847864430817 | 99.7856
S54553 | Butler Maple | EnergyRatio | Pass | Pass |  | 95.0215
S54553 | Butler Maple | ProductionEnergy | Pass | Pass |  | 100
S54553 | Butler Maple | PVlosses | Pass | Pass |  | 100
S54553 | Butler Maple | PVmodelEnergy24 | Pass | Pass |  | 103.3879
S54553 | Butler Maple | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S54613 | Warbler | Availability | Fail | Fail | Fail: 0.00 % Sungrow SG125 Inverter A1 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A2 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A3 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A4 at 100%: Availability: 95.74468085106383 % Sungrow SG125 Inverter A5 at 100%: Availability: 95.74468085106383 % Sungrow SG125 Inverter A6 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A7 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A8 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A9 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A10 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A11 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A12 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A13 at 100%: Availability: 95.74468085106383 % Sungrow SG125 Inverter A14 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter A15 at 100%: Availability: 95.74468085106383 % Sungrow SG125 Inverter A16 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B17 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B18 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B20 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B21 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B22 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B23 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B24 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B25 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B26 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B27 at 100%: Availability: 95.74468085106383 % Sungrow SG125 Inverter B28 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B29 at 100%: Availability: 95.74468085106383 % Sungrow SG125 Inverter B30 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B31 at 100%: Availability: 97.87234042553192 % Sungrow SG125 Inverter B32 at 100%: Availability: 97.87234042553192 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 97.87234042553192\t %', 'success': 0.0, 'hardwareKey': 'H263557', 'hardwareName': 'Sungrow SG125 Inverter A1 at 100%', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 97.87234042553192\t %', 'success': 0.0, 'hardwareKey': 'H263558', 'hardwareName': 'Sungrow SG125 Inverter A2 at 100%', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Availability: \t\t\t 97.87234042553192\t %', 'success': 0.0, 'hardwareKey': 'H263559', 'hardwareName': 'Sungrow SG125 Inverter A3 at 100%', 'isAcknowledged': False}
S54613 | Warbler | CheckUpload | Pass | Pass |  | 100
S54613 | Warbler | InverterUptime | Fail | Fail | Fail: 0.00 % Sungrow SG125 Inverter A1 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A2 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A3 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A4 at 100%: Inverter uptime: 95.7446808510638 % Sungrow SG125 Inverter A5 at 100%: Inverter uptime: 95.7446808510638 % Sungrow SG125 Inverter A6 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A7 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A8 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A9 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A10 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A11 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A12 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A13 at 100%: Inverter uptime: 95.7446808510638 % Sungrow SG125 Inverter A14 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter A15 at 100%: Inverter uptime: 95.7446808510638 % Sungrow SG125 Inverter A16 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B17 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B18 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B20 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B21 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B22 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B23 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B24 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B25 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B26 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B27 at 100%: Inverter uptime: 95.7446808510638 % Sungrow SG125 Inverter B28 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B29 at 100%: Inverter uptime: 95.7446808510638 % Sungrow SG125 Inverter B30 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B31 at 100%: Inverter uptime: 97.8723404255319 % Sungrow SG125 Inverter B32 at 100%: Inverter uptime: 97.8723404255319 % 31 of 32 inverters failed to achieve an uptime of 100 % | 0 | {'index': 0, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 97.8723404255319\t %', 'success': 0.0, 'hardwareKey': 'H263557', 'hardwareName': 'Sungrow SG125 Inverter A1 at 100%', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 97.8723404255319\t %', 'success': 0.0, 'hardwareKey': 'H263558', 'hardwareName': 'Sungrow SG125 Inverter A2 at 100%', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 97.8723404255319\t %', 'success': 0.0, 'hardwareKey': 'H263559', 'hardwareName': 'Sungrow SG125 Inverter A3 at 100%', 'isAcknowledged': False}
S54613 | Warbler | NetworkCom | Pass | Pass | Pass: 100.00 % PowerManager 2200: 3 of 3 TCP devices communicating normally PowerManager 2200: 16 of 16 devices on port 1 communicating normally PowerManager 2200: 16 of 16 devices on port 2 communicating normally PowerManager 2200: 4 of 4 devices on port 4 communicating normally | 100
S54613 | Warbler | AlertRecipients | Pass | Pass |  | 100
S54613 | Warbler | CheckHW | Pass | Pass |  | 100
S54613 | Warbler | CheckSysSize | Pass | Pass |  | 100
S54613 | Warbler | DefaultAlerts | Pass | Pass |  | 100
S54613 | Warbler | HasPVmodel | Pass | Pass |  | 100
S54613 | Warbler | HasWSmodel | Pass | Pass |  | 100
S54613 | Warbler | InvalidAlerts | Pass | Pass |  | 100
S54613 | Warbler | SiteConfig | Pass | Pass |  | 100
S54613 | Warbler | CheckMeterVoltage | Pass | Pass |  | 100
S54613 | Warbler | CheckWeather | Pass | Pass |  | 100
S54613 | Warbler | DataCuration | Pass | Pass |  | 100
S54613 | Warbler | kWandkWh | Pass | Pass |  | 100
S54613 | Warbler | PVPMenergy | Pass | Pass | SEL 735 Production Meter: Inverter / meter energy correlation: % | 98.8046
S54613 | Warbler | CheckPMCTs | Pass | Pass | SEL 735 Production Meter: Phase current ratio 99.79381443298969 %, PF: 1 | 99.7938
S54613 | Warbler | EnergyRatio | Pass | Pass |  | 89.8863
S54613 | Warbler | ProductionEnergy | Pass | Pass |  | 100
S54613 | Warbler | PVlosses | Pass | Pass |  | 100
S54613 | Warbler | PVmodelEnergy24 | Pass | Pass |  | 89.8861
S54613 | Warbler | CorrectiveAction | Pass | Pass | Slight losses or device availability issues should be addressed during the next scheduled maintenance activity. | 95
S54681 | Eagle | Availability | Fail | Fail | Fail: 0.00 % Cell Modem Reporting (RV50): Availability: 0 % PowerLogger 1000 (SO95895): Availability: 0 % Elkor Production Meter: Availability: 0 % Weather Station 1 (Standard w/ Kipp POA): Availability: 0 % Weather Station 2 (Kipp GHI & Mod Temp): Availability: 0 % Availability, all inverters: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H264340', 'hardwareName': 'Cell Modem Reporting (RV50)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H502645', 'hardwareName': 'PowerLogger 1000 (SO95895)', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H264342', 'hardwareName': 'Elkor Production Meter', 'isAcknowledged': False}
S54681 | Eagle | CheckUpload | Fail | Fail | Fail: 0.00 % PowerLogger 1000 (SO95895): Data acquisition system and all connected devices are offline. Last upload: 6/6/2026 3:08 PM ( US/Eastern ), delay: 1 d 19.4 h Cell Modem Reporting (RV50): Last upload: 6/6/2026 3:05 PM ( US/Eastern ), delay: 1 d 19.5 h | 0 | {'index': 0, 'result': 3, 'detail': 'Data acquisition system and all connected devices are offline. Last upload: \t\t\t 6/6/2026 3:08 PM\t (\t\t\t US/Eastern\t), delay: \t\t\t 1 d 19.4 h\t', 'success': 0.0, 'hardwareKey': 'H502645', 'hardwareName': 'PowerLogger 1000 (SO95895)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Last upload: \t\t\t 6/6/2026 3:05 PM\t (\t\t\t US/Eastern\t), delay: \t\t\t 1 d 19.5 h\t', 'success': 0.0, 'hardwareKey': 'H264340', 'hardwareName': 'Cell Modem Reporting (RV50)', 'isAcknowledged': False}
S54681 | Eagle | NetworkCom | Fail | Fail | PowerLogger 1000 (SO95895): Data logger not uploading | 0 | {'index': 0, 'result': 3, 'detail': 'Data logger not uploading', 'success': 0.0, 'hardwareKey': 'H502645', 'hardwareName': 'PowerLogger 1000 (SO95895)', 'isAcknowledged': False}
S54681 | Eagle | AlertRecipients | Pass | Pass |  | 100
S54681 | Eagle | CheckHW | Fail | Fail | Function ID conflict on : | 0 | {'index': 0, 'result': 3, 'detail': 'Function ID conflict on : ', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S54681 | Eagle | CheckSysSize | Pass | Pass |  | 100
S54681 | Eagle | DefaultAlerts | Pass | Pass |  | 100
S54681 | Eagle | HasPVmodel | Pass | Pass |  | 100
S54681 | Eagle | HasWSmodel | Pass | Pass |  | 100
S54681 | Eagle | InvalidAlerts | Fail | Fail | Site alert ' Rule Tool Alert ' ( 126551249 ) doesn't have an active configuration. | 0 | {'index': 0, 'result': 3, 'detail': "Site alert '\t\t\t Rule Tool Alert\t' (\t\t\t 126551249\t) doesn't have an active configuration.", 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S54681 | Eagle | SiteConfig | Pass | Pass |  | 100
S54681 | Eagle | CheckWeather | Fail | Fail | Fail: 0.00 % Weather Station 1 (Standard w/ Kipp POA): Invalid ambient temperature Weather Station 1 (Standard w/ Kipp POA): Invalid module temperature Weather Station 1 (Standard w/ Kipp POA): Invalid irradiance: Weather Station 2 (Kipp GHI & Mod Temp): Invalid module temperature Weather Station 2 (Kipp GHI & Mod Temp): Invalid irradiance: | 0 | {'index': 0, 'result': 3, 'detail': 'Invalid ambient temperature', 'success': 0.0, 'hardwareKey': 'H264368', 'hardwareName': 'Weather Station 1 (Standard w/ Kipp POA)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Invalid module temperature ', 'success': 0.0, 'hardwareKey': 'H264368', 'hardwareName': 'Weather Station 1 (Standard w/ Kipp POA)', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Invalid irradiance: ', 'success': 0.0, 'hardwareKey': 'H264368', 'hardwareName': 'Weather Station 1 (Standard w/ Kipp POA)', 'isAcknowledged': False}
S54681 | Eagle | DataCuration | Pass | Pass |  | 100
S54681 | Eagle | kWandkWh | Pass | Pass |  | 100
S54681 | Eagle | PVPMenergy | Fail | Fail | Elkor Production Meter: Energy data not found | 0 | {'index': 0, 'result': 3, 'detail': 'Energy data not found', 'success': 0.0, 'hardwareKey': 'H264342', 'hardwareName': 'Elkor Production Meter', 'isAcknowledged': False}
S54681 | Eagle | EnergyRatio | Fail | Fail | Elkor Production Meter: Unable to calculate energy ratio | 0 | {'index': 0, 'result': 3, 'detail': 'Unable to calculate energy ratio', 'success': 0.0, 'hardwareKey': 'H264342', 'hardwareName': 'Elkor Production Meter', 'isAcknowledged': False}
S54681 | Eagle | ProductionEnergy | Pass | Pass |  | 100
S54681 | Eagle | PVlosses | Fail | Fail | Fail: 0.00 % CPS SCH125kTL Inv - 1: Unable to calculate PV losses CPS SCH125kTL Inv - 2: Unable to calculate PV losses CPS SCH125kTL Inv - 3: Unable to calculate PV losses CPS SCH125kTL Inv - 4: Unable to calculate PV losses CPS SCH125kTL Inv - 5: Unable to calculate PV losses CPS SCH125kTL Inv - 6: Unable to calculate PV losses CPS SCH125kTL Inv - 7: Unable to calculate PV losses CPS SCH125kTL Inv - 8: Unable to calculate PV losses CPS SCH125kTL Inv - 9: Unable to calculate PV losses CPS SCH125kTL Inv - 10: Unable to calculate PV losses CPS SCH125kTL Inv - 11: Unable to calculate PV losses CPS SCH125kTL Inv - 12: Unable to calculate PV losses CPS SCH125kTL Inv - 13: Unable to calculate PV losses CPS SCH125kTL Inv - 14: Unable to calculate PV losses CPS SCH125kTL Inv - 15: Unable to calculate PV losses CPS SCH125kTL Inv - 16: Unable to calculate PV losses CPS SCH125kTL Inv - 17: Unable to calculate PV losses CPS SCH125kTL Inv - 18: Unable to calculate PV losses CPS SCH125kTL Inv - 19: Unable to calculate PV losses CPS SCH125kTL Inv - 20: Unable to calculate PV losses CPS SCH125kTL Inv - 21: Unable to calculate PV losses CPS SCH125kTL Inv - 22: Unable to calculate PV losses CPS SCH125kTL Inv - 23: Unable to calculate PV losses CPS SCH125kTL Inv - 24: Unable to calculate PV losses | 0 | {'index': 0, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H264344', 'hardwareName': 'CPS SCH125kTL Inv - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H264345', 'hardwareName': 'CPS SCH125kTL Inv - 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H264346', 'hardwareName': 'CPS SCH125kTL Inv - 3', 'isAcknowledged': False}
S54681 | Eagle | PVmodelEnergy24 | Fail | Fail | Unable to calculate expected energy | 0 | {'index': 0, 'result': 3, 'detail': 'Unable to calculate expected energy', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S54681 | Eagle | CorrectiveAction | Fail | Fail | Fail: 0.00 % Equipment repair required. Data acquisition system offline , Gateway : PowerLogger 1000 (SO95895) Equipment repair required. Low availability , Cell modem, Gateway : Cell Modem Reporting (RV50), PowerLogger 1000 (SO95895) | 0 | {'index': 0, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Data acquisition system offline\t, \t\t\t Gateway\t: \t\t\t PowerLogger 1000 (SO95895)\t', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Low availability\t, \t\t\t Cell modem, Gateway\t: \t\t\t Cell Modem Reporting (RV50), PowerLogger 1000 (SO95895)\t', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S55935 | Manuel Lawrence Dairy | Availability | Fail | Fail | Availability, all inverters: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability, all inverters: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S55935 | Manuel Lawrence Dairy | CheckUpload | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | NetworkCom | Pass | Pass | Pass: 100.00 % PowerLogger 1000: 1 of 1 TCP devices communicating normally PowerLogger 1000: 2 of 2 devices on port 2 communicating normally PowerLogger 1000: 15 of 15 devices on port 1 communicating normally | 100
S55935 | Manuel Lawrence Dairy | AlertRecipients | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | CheckHW | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | CheckSysSize | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | DefaultAlerts | Fail | Fail | Solar Tracker (SFR TDP 2.0): Default alerts not set: 3635 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 3635\t', 'success': 0.0, 'hardwareKey': 'H278599', 'hardwareName': 'Solar Tracker (SFR TDP 2.0)', 'isAcknowledged': False}
S55935 | Manuel Lawrence Dairy | HasPVmodel | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | HasWSmodel | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | InvalidAlerts | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | SiteConfig | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | CheckMeterVoltage | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | CheckWeather | Fail | Fail | Fail: 0.00 % IMT Ref. Cell (w/ Mod): Invalid module temperature IMT Ref. Cell (w/ Mod): Invalid irradiance: | 0 | {'index': 0, 'result': 3, 'detail': 'Invalid module temperature ', 'success': 0.0, 'hardwareKey': 'H278620', 'hardwareName': 'IMT Ref. Cell (w/ Mod)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Invalid irradiance: ', 'success': 0.0, 'hardwareKey': 'H278620', 'hardwareName': 'IMT Ref. Cell (w/ Mod)', 'isAcknowledged': False}
S55935 | Manuel Lawrence Dairy | DataCuration | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | kWandkWh | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | PVPMenergy | Pass | Pass | Elkor Production Meter: Inverter / meter energy correlation: % | 99.2982
S55935 | Manuel Lawrence Dairy | Tracker | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | CheckPMCTs | Pass | Pass | Elkor Production Meter: Phase current ratio 99.0820685413414 %, PF: 0.9987769015353273 | 99.0821
S55935 | Manuel Lawrence Dairy | EnergyRatio | Fail | Fail | Elkor Production Meter: Unable to calculate energy ratio | 0 | {'index': 0, 'result': 3, 'detail': 'Unable to calculate energy ratio', 'success': 0.0, 'hardwareKey': 'H278595', 'hardwareName': 'Elkor Production Meter', 'isAcknowledged': False}
S55935 | Manuel Lawrence Dairy | ProductionEnergy | Pass | Pass |  | 100
S55935 | Manuel Lawrence Dairy | PVlosses | Fail | Fail | Fail: 0.00 % CPS SCA 60KTL-DO INV - 1: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 2: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 3: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 4: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 5: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 6: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 7: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 8: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 9: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 10: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 11: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 12: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 13: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 14: Unable to calculate PV losses CPS SCA 60KTL-DO INV - 15: Unable to calculate PV losses | 0 | {'index': 0, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H278604', 'hardwareName': 'CPS SCA 60KTL-DO INV - 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H278605', 'hardwareName': 'CPS SCA 60KTL-DO INV - 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H278606', 'hardwareName': 'CPS SCA 60KTL-DO INV - 3', 'isAcknowledged': False}
S55935 | Manuel Lawrence Dairy | PVmodelEnergy24 | Fail | Fail | Energy above expected ( ∞ %) | NaN | {'index': 0, 'result': 3, 'detail': 'Energy above expected (\t\t\t ∞\t %)', 'success': 'Infinity', 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S55935 | Manuel Lawrence Dairy | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S59656 | Whitetail | Availability | Fail | Fail | Fail: 0.00 % GameChange Tracker Control: Availability: 0 % GameChange Tracker Control 2.3: Availability: 87.36842105263159 % GameChange Tracker Control 2.2: Availability: 87.36842105263159 % GameChange Tracker Control 2.1: Availability: 86.31578947368422 % 16 String Inverters: Availability: 0 % 17 String Inverters: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H312486', 'hardwareName': 'GameChange Tracker Control', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 87.36842105263159\t %', 'success': 0.0, 'hardwareKey': 'H590015', 'hardwareName': 'GameChange Tracker Control 2.3', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Availability: \t\t\t 87.36842105263159\t %', 'success': 0.0, 'hardwareKey': 'H590016', 'hardwareName': 'GameChange Tracker Control 2.2', 'isAcknowledged': False}
S59656 | Whitetail | CheckUpload | Fail | Fail | Fail: 0.00 % SunGrow SG125HV - Inverter 60: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 62: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 64: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 65: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 66: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 67: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 68: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 69: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 70: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 71: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 73: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 74: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 75: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 76: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 77: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 78: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 79: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h SunGrow SG125HV - Inverter 80: Last upload: 6/8/2026 4:45 AM ( US/Eastern ), delay: 0.5 h Weather Station (Standard): Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h Hukseflux SR-30 - POA: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h Hukseflux SR-30 - GHI: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h GameChange Tracker Control: Last upload: 6/14/2024 7:15 AM ( US/Eastern ), delay: 723 d 22.0 h AE Smart UPS: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h GameChange Tracker Control 2.1: Last upload: 6/8/2026 4:44 AM ( US/Eastern ), delay: 0.5 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 6/8/2026 4:44 AM\t (\t\t\t US/Eastern\t), delay: \t\t\t 0.5 h\t', 'success': 0.0, 'hardwareKey': 'H312448', 'hardwareName': 'SunGrow SG125HV - Inverter 60', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Last upload: \t\t\t 6/8/2026 4:45 AM\t (\t\t\t US/Eastern\t), delay: \t\t\t 0.5 h\t', 'success': 0.0, 'hardwareKey': 'H312450', 'hardwareName': 'SunGrow SG125HV - Inverter 62', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Last upload: \t\t\t 6/8/2026 4:45 AM\t (\t\t\t US/Eastern\t), delay: \t\t\t 0.5 h\t', 'success': 0.0, 'hardwareKey': 'H312452', 'hardwareName': 'SunGrow SG125HV - Inverter 64', 'isAcknowledged': False}
S59656 | Whitetail | InverterUptime | Pass | Pass |  | 100
S59656 | Whitetail | NetworkCom | Pass | Pass | Pass: 100.00 % PowerManager 2200 (RMA16217/SO101810): 47 of 68 TCP devices communicating normally PowerManager 2200 (RMA16217/SO101810): 32 of 40 devices on port 1 communicating normally PowerManager 2200 (RMA16217/SO101810): 30 of 40 devices on port 2 communicating normally PowerManager 2200 (RMA16217/SO101810): 1 of 3 devices on port 4 communicating normally PowerManager 2200 (RMA16217/SO101810): 1 of 2 devices on port 3 communicating normally | 100
S59656 | Whitetail | AlertRecipients | Pass | Pass |  | 100
S59656 | Whitetail | CheckHW | Fail | Fail | Fail: 0.00 % GameChange Tracker Control 2.3: Multiple devices on : GameChange Tracker Control 2.3: Suggested tracker configuration, Initial angle: , GCR: , GCR West: GameChange Tracker Control 2.2: Suggested tracker configuration, Initial angle: , GCR: , GCR West: GameChange Tracker Control 2.1: Suggested tracker configuration, Initial angle: , GCR: , GCR West: 16 String Inverters: Inverter group devices that don't receive data should be set to 'Offline'. 17 String Inverters: Inverter group devices that don't receive data should be set to 'Offline'. | 0 | {'index': 0, 'result': 3, 'detail': 'Multiple devices on : ', 'success': 0.0, 'hardwareKey': 'H590015', 'hardwareName': 'GameChange Tracker Control 2.3', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Suggested tracker configuration, Initial angle: , GCR: , GCR West: ', 'success': 0.0, 'hardwareKey': 'H590015', 'hardwareName': 'GameChange Tracker Control 2.3', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Suggested tracker configuration, Initial angle: , GCR: , GCR West: ', 'success': 0.0, 'hardwareKey': 'H590016', 'hardwareName': 'GameChange Tracker Control 2.2', 'isAcknowledged': False}
S59656 | Whitetail | CheckSysSize | Pass | Pass |  | 100
S59656 | Whitetail | DefaultAlerts | Pass | Pass |  | 100
S59656 | Whitetail | HasPVmodel | Pass | Pass |  | 100
S59656 | Whitetail | HasWSmodel | Pass | Pass |  | 100
S59656 | Whitetail | InvalidAlerts | Fail | Fail | GameChange Tracker Control 2.1: Alert ' Gamechange Tracker Alert ' triggered 14 times in the past 24 hours. | 0 | {'index': 0, 'result': 3, 'detail': "Alert '\t\t\t Gamechange Tracker Alert\t' triggered \t\t\t 14\t times in the past 24 hours.", 'success': 0.0, 'hardwareKey': 'H590017', 'hardwareName': 'GameChange Tracker Control 2.1', 'isAcknowledged': False}
S59656 | Whitetail | SiteConfig | Pass | Pass |  | 100
S59656 | Whitetail | CheckMeterVoltage | Pass | Pass |  | 100
S59656 | Whitetail | CheckWeather | Fail | Fail | Fail: 0.00 % Hukseflux SR-30 - POA: The POA sensor, "", appears to be fixed tilt and is configured for a tracker. Hukseflux SR-30 - GHI: Insolation mismatch 93.97857410646029 %, check azimuth/tilt settings: Sun (GHI Temp comp) (this is a secondary sensor) Hukseflux SR-30 - POA: Insolation mismatch + 66.75210599308807 % (higher than other sensors), check azimuth/tilt settings: Sun (POA Temp comp) Hukseflux SR-30 - ALB: Insolation mismatch -88.81360574686165 %, check azimuth/tilt settings: Sun (POA Temp comp) (this is a secondary sensor) | 0 | {'index': 0, 'result': 3, 'detail': 'The POA sensor, "", appears to be fixed tilt and is configured for a tracker.', 'success': 0.0, 'hardwareKey': 'H312487', 'hardwareName': 'Hukseflux SR-30 - POA', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Insolation mismatch +\t\t\t 66.75210599308807\t % (higher than other sensors), check azimuth/tilt settings: \t\t\t Sun (POA Temp comp)\t', 'success': 0.0, 'hardwareKey': 'H312487', 'hardwareName': 'Hukseflux SR-30 - POA', 'isAcknowledged': False}
S59656 | Whitetail | DataCuration | Pass | Pass |  | 100
S59656 | Whitetail | kWandkWh | Pass | Pass |  | 100
S59656 | Whitetail | PVPMenergy | Pass | Pass | SEL-735 Production Meter: Inverter / meter energy correlation: % | 98.8955
S59656 | Whitetail | Tracker | Fail | Fail | Fail: 0.00 % GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 181 ): 51.4146 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 182 ): 51.2478 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 183 ): 51.21281 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 184 ): 51.24342 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 185 ): 51.05818 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 186 ): 51.03223 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 187 ): 51.30563 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 188 ): 51.29284 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 189 ): 51.2625 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 190 ): 51.53758 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 191 ): 51.35439 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 192 ): 51.17891 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 193 ): 51.34066 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 194 ): 51.33859 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 195 ): 51.35929 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 196 ): 51.15088 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 197 ): 51.43265 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 198 ): 51.29 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 199 ): 51.18159 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 200 ): 51.24629 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 201 ): 51.19966 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 202 ): 51.3382 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 203 ): 51.23331 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 204 ): 51.1298 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 205 ): 51.0869 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 206 ): 51.49611 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 207 ): 51.42662 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 208 ): 51.02481 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 209 ): 51.28318 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 210 ): 51.30578 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 211 ): 51.36145 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 212 ): 51.23743 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 213 ): 51.26388 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 214 ): 51.38951 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 215 ): 51.42027 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 216 ): 51.3428 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 217 ): 51.27765 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 218 ): 51.23572 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 219 ): 51.36942 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 220 ): 51.27112 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 221 ): 51.39877 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 222 ): 51.31349 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 223 ): 50.94708 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 224 ): 51.11267 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 225 ): 51.34988 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 226 ): 51.13349 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 227 ): 51.18684 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 228 ): 51.28625 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 229 ): 51.40151 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 230 ): 51.35184 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 231 ): 51.37937 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 232 ): 51.41435 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 233 ): 51.25137 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 234 ): 51.43608 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 235 ): 51.19122 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 236 ): 51.30472 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 237 ): 51.15827 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 238 ): 51.07985 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 239 ): 51.10832 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 240 ): 51.33655 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 241 ): 51.26604 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 242 ): 51.43687 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 243 ): 51.03088 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 244 ): 51.23346 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 245 ): 51.3043 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 246 ): 51.36159 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 247 ): 51.48622 degrees GameChange Tracker Control 2.3: Average tracker error ( Panel/table angle 248 ): 51.27886 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 91 ): 50.85713 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 92 ): 50.90562 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 93 ): 50.80977 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 94 ): 50.98461 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 95 ): 50.63884 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 96 ): 50.81773 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 97 ): 50.9264 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 98 ): 50.81937 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 99 ): 50.79919 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 100 ): 50.82214 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 101 ): 50.68666 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 102 ): 50.68729 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 103 ): 50.56039 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 104 ): 50.7287 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 105 ): 50.83253 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 106 ): 50.80819 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 107 ): 50.84415 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 108 ): 50.79514 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 109 ): 50.72114 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 110 ): 50.71922 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 111 ): 50.67 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 112 ): 50.79303 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 113 ): 50.75875 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 114 ): 50.93186 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 115 ): 50.8661 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 116 ): 50.90091 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 117 ): 50.72829 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 118 ): 50.79821 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 119 ): 50.88062 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 120 ): 50.87989 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 121 ): 50.79494 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 122 ): 50.71849 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 123 ): 50.51905 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 124 ): 50.82372 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 125 ): 50.74075 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 126 ): 50.79153 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 127 ): 50.87178 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 128 ): 50.83823 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 129 ): 50.8196 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 130 ): 50.92421 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 131 ): 50.91248 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 132 ): 51.26749 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 133 ): 50.81844 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 134 ): 50.88978 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 135 ): 50.80846 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 136 ): 50.81663 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 137 ): 50.82093 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 138 ): 50.5583 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 139 ): 50.82161 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 140 ): 50.90508 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 141 ): 50.80292 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 142 ): 50.88922 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 143 ): 50.77883 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 144 ): 50.96988 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 145 ): 50.78896 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 146 ): 50.85383 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 147 ): 50.69926 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 148 ): 50.79797 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 149 ): 50.94099 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 150 ): 50.8615 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 151 ): 50.96487 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 152 ): 50.84415 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 153 ): 50.85366 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 154 ): 50.84642 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 155 ): 50.8466 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 156 ): 50.59919 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 157 ): 50.7506 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 158 ): 51.11673 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 159 ): 50.81052 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 160 ): 50.91735 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 161 ): 50.7654 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 162 ): 50.9581 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 163 ): 50.75088 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 164 ): 50.66079 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 165 ): 50.93233 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 166 ): 50.96505 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 167 ): 50.9107 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 168 ): 50.91373 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 169 ): 50.68422 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 170 ): 50.48921 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 171 ): 50.63815 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 172 ): 50.9485 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 173 ): 50.89591 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 174 ): 50.70155 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 175 ): 50.79074 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 176 ): 50.71186 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 177 ): 50.71186 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 178 ): 50.84393 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 179 ): 50.74636 degrees GameChange Tracker Control 2.2: Average tracker error ( Panel/table angle 180 ): 50.76708 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 1 ): 51.19713 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 2 ): 51.04853 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 3 ): 51.22002 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 4 ): 51.25511 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 5 ): 51.37716 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 6 ): 51.1465 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 7 ): 50.97634 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 8 ): 51.25089 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 9 ): 51.13964 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 10 ): 51.22431 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 11 ): 51.17404 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 12 ): 51.28304 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 13 ): 51.30839 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 14 ): 51.18396 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 15 ): 51.20217 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 16 ): 51.26894 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 17 ): 51.25692 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 18 ): 51.06623 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 19 ): 51.15756 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 20 ): 51.14151 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 21 ): 51.20723 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 22 ): 51.21891 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 23 ): 51.96844 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 24 ): 51.29129 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 25 ): 51.27504 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 26 ): 51.17369 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 27 ): 51.21637 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 28 ): 51.29768 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 29 ): 50.96143 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 30 ): 51.27106 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 31 ): 51.26459 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 32 ): 51.21504 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 33 ): 51.24469 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 34 ): 51.23243 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 35 ): 51.20557 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 36 ): 51.05984 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 37 ): 51.06121 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 38 ): 51.15962 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 39 ): 51.23615 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 40 ): 51.01456 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 41 ): 51.12667 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 42 ): 51.33819 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 43 ): 51.28112 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 44 ): 51.24694 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 45 ): 51.3037 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 46 ): 51.23223 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 47 ): 51.22517 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 48 ): 51.11038 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 49 ): 51.06104 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 50 ): 50.89095 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 51 ): 51.22916 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 52 ): 51.14045 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 53 ): 51.30383 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 54 ): 51.87591 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 55 ): 51.12674 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 56 ): 51.34002 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 57 ): 51.16833 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 58 ): 51.2649 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 59 ): 51.29316 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 60 ): 39.19302 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 61 ): 50.88567 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 62 ): 51.14808 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 63 ): 51.13657 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 64 ): 51.18206 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 65 ): 51.1874 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 66 ): 51.24683 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 67 ): 51.21074 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 68 ): 51.27037 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 69 ): 51.23204 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 70 ): 51.38671 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 71 ): 51.24775 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 72 ): 51.09451 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 73 ): 51.36522 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 74 ): 51.17777 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 75 ): 51.23125 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 76 ): 51.16987 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 77 ): 51.10846 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 78 ): 51.20258 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 79 ): 51.12797 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 80 ): 51.20684 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 81 ): 51.18868 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 82 ): 51.2146 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 83 ): 51.21538 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 84 ): 51.37437 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 85 ): 51.2684 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 86 ): 51.08355 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 87 ): 51.15176 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 88 ): 51.14454 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 89 ): 51.08844 degrees GameChange Tracker Control 2.1: Average tracker error ( Panel/table angle 90 ): 51.25107 degrees | 0 | {'index': 0, 'result': 3, 'detail': 'Average tracker error (\t\t\t Panel/table angle 181\t): \t\t\t 51.4146\t degrees', 'success': 0.0, 'hardwareKey': 'H590015', 'hardwareName': 'GameChange Tracker Control 2.3', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Average tracker error (\t\t\t Panel/table angle 182\t): \t\t\t 51.2478\t degrees', 'success': 0.0, 'hardwareKey': 'H590015', 'hardwareName': 'GameChange Tracker Control 2.3', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Average tracker error (\t\t\t Panel/table angle 183\t): \t\t\t 51.21281\t degrees', 'success': 0.0, 'hardwareKey': 'H590015', 'hardwareName': 'GameChange Tracker Control 2.3', 'isAcknowledged': False}
S59656 | Whitetail | CheckPMCTs | Pass | Pass | SEL-735 Production Meter: Phase current ratio 99.69705192117286 %, PF: 0.980000003315249 | 99.6971
S59656 | Whitetail | EnergyRatio | Pass | Pass |  | 90.4033
S59656 | Whitetail | ProductionEnergy | Pass | Pass |  | 100
S59656 | Whitetail | PVlosses | Pass | Pass |  | 100
S59656 | Whitetail | PVmodelEnergy24 | Pass | Pass |  | 95.7261
S59656 | Whitetail | CorrectiveAction | Fail | Fail | Equipment repair required. Low availability , Solar tracker, Inverter group : GameChange Tracker Control, GameChange Tracker Control 2.3, GameChange Tracker Control 2.2, GameChange Tracker Control 2.1, 16 String Inverters, 17 String Inverters | 50 | {'index': 0, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Low availability\t, \t\t\t Solar tracker, Inverter group\t: \t\t\t GameChange Tracker Control, GameChange Tracker Control 2.3, GameChange Tracker Control 2.2, GameChange Tracker Control 2.1, 16 String Inverters, 17 String Inverters\t', 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S63837 | Bulloch 1B | Availability | Pass | Pass |  | 100
S63837 | Bulloch 1B | CheckUpload | Fail | Fail | iPRO Security Camera: Last upload: 6/7/2026 11:41 PM ( US/Eastern ), delay: 5.0 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 6/7/2026 11:41 PM\t (\t\t\t US/Eastern\t), delay: \t\t\t 5.0 h\t', 'success': 0.0, 'hardwareKey': 'H399369', 'hardwareName': 'iPRO Security Camera', 'isAcknowledged': False}
S63837 | Bulloch 1B | InverterUptime | Pass | Pass |  | 100
S63837 | Bulloch 1B | NetworkCom | Pass | Pass | Pass: 100.00 % PowerManager 2200 (RMA14348): 17 of 18 TCP devices communicating normally PowerManager 2200 (RMA14348): 24 of 24 devices on port 1 communicating normally PowerManager 2200 (RMA14348): 4 of 4 devices on port 4 communicating normally | 100
S63837 | Bulloch 1B | AlertRecipients | Pass | Pass |  | 100
S63837 | Bulloch 1B | CheckHW | Pass | Pass |  | 100
S63837 | Bulloch 1B | CheckSysSize | Pass | Pass |  | 100
S63837 | Bulloch 1B | DefaultAlerts | Fail | Fail | AE Smart UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H399368', 'hardwareName': 'AE Smart UPS', 'isAcknowledged': False}
S63837 | Bulloch 1B | HasPVmodel | Pass | Pass |  | 100
S63837 | Bulloch 1B | HasWSmodel | Pass | Pass |  | 100
S63837 | Bulloch 1B | InvalidAlerts | Pass | Pass |  | 100
S63837 | Bulloch 1B | SiteConfig | Pass | Pass |  | 100
S63837 | Bulloch 1B | CheckMeterVoltage | Pass | Pass |  | 100
S63837 | Bulloch 1B | CheckWeather | Pass | Pass |  | 100
S63837 | Bulloch 1B | DataCuration | Pass | Pass |  | 100
S63837 | Bulloch 1B | kWandkWh | Pass | Pass |  | 100
S63837 | Bulloch 1B | PVPMenergy | Pass | Pass | ION 8650 Production Meter: Inverter / meter energy correlation: % | 96.9123
S63837 | Bulloch 1B | Tracker | Fail | Fail | Fail: 0.00 % Tracker Control: Tracker ' Position A1 S 22 ' always 0.0104797 degrees Tracker Control: Tracker ' Position A1 S 54 ' always -4.0196 degrees Tracker Control: Tracker ' Position A1 S 79 ' always 46.8563 degrees Tracker Control: Average tracker error ( Position A1 S 1 ): 6.239625 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 22\t' always \t\t\t 0.0104797\t degrees", 'success': 0.0, 'hardwareKey': 'H399367', 'hardwareName': 'Tracker Control', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 54\t' always \t\t\t -4.0196\t degrees", 'success': 0.0, 'hardwareKey': 'H399367', 'hardwareName': 'Tracker Control', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 79\t' always \t\t\t 46.8563\t degrees", 'success': 0.0, 'hardwareKey': 'H399367', 'hardwareName': 'Tracker Control', 'isAcknowledged': False}
S63837 | Bulloch 1B | CheckPMCTs | Pass | Pass | ION 8650 Production Meter: Phase current ratio 99.7178319985732 %, PF: 0.9983805058084539 | 99.7178
S63837 | Bulloch 1B | EnergyRatio | Pass | Pass |  | 93.5739
S63837 | Bulloch 1B | ProductionEnergy | Pass | Pass |  | 100
S63837 | Bulloch 1B | PVlosses | Pass | Pass |  | 100
S63837 | Bulloch 1B | PVmodelEnergy24 | Pass | Pass |  | 100.9739
S63837 | Bulloch 1B | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S63838 | Bulloch 1A | Availability | Pass | Pass |  | 100
S63838 | Bulloch 1A | CheckUpload | Pass | Pass |  | 100
S63838 | Bulloch 1A | InverterUptime | Pass | Pass |  | 100
S63838 | Bulloch 1A | NetworkCom | Pass | Pass | Pass: 100.00 % PowerManager 2200: 18 of 18 TCP devices communicating normally PowerManager 2200: 24 of 24 devices on port 1 communicating normally PowerManager 2200: 4 of 4 devices on port 4 communicating normally | 100
S63838 | Bulloch 1A | AlertRecipients | Pass | Pass |  | 100
S63838 | Bulloch 1A | CheckHW | Pass | Pass |  | 100
S63838 | Bulloch 1A | CheckSysSize | Pass | Pass |  | 100
S63838 | Bulloch 1A | DefaultAlerts | Fail | Fail | AE Smart UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H400687', 'hardwareName': 'AE Smart UPS', 'isAcknowledged': False}
S63838 | Bulloch 1A | HasPVmodel | Pass | Pass |  | 100
S63838 | Bulloch 1A | HasWSmodel | Pass | Pass |  | 100
S63838 | Bulloch 1A | InvalidAlerts | Pass | Pass |  | 100
S63838 | Bulloch 1A | SiteConfig | Pass | Pass |  | 100
S63838 | Bulloch 1A | CheckMeterVoltage | Pass | Pass |  | 100
S63838 | Bulloch 1A | CheckWeather | Pass | Pass |  | 100
S63838 | Bulloch 1A | DataCuration | Pass | Pass |  | 100
S63838 | Bulloch 1A | kWandkWh | Pass | Pass |  | 100
S63838 | Bulloch 1A | PVPMenergy | Pass | Pass | ION 8650 Production Meter: Inverter / meter energy correlation: % | 97.9881
S63838 | Bulloch 1A | Tracker | Fail | Fail | FlexRack Tracker Control: Tracker ' Position A1 S 16 ' always 0 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 16\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H400684', 'hardwareName': 'FlexRack Tracker Control', 'isAcknowledged': False}
S63838 | Bulloch 1A | CheckPMCTs | Pass | Pass | ION 8650 Production Meter: Phase current ratio 99.66923623640042 %, PF: 0.99820077097973 | 99.6692
S63838 | Bulloch 1A | EnergyRatio | Pass | Pass |  | 97.2571
S63838 | Bulloch 1A | ProductionEnergy | Pass | Pass |  | 100
S63838 | Bulloch 1A | PVlosses | Pass | Pass |  | 100
S63838 | Bulloch 1A | PVmodelEnergy24 | Pass | Pass |  | 98.2043
S63838 | Bulloch 1A | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S63839 | Richmond | Availability | Fail | Fail | Fail: 0.00 % 10 String INV's: Availability: 0 % 11 String INV's: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H465413', 'hardwareName': "10 String INV's", 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H465414', 'hardwareName': "11 String INV's", 'isAcknowledged': False}
S63839 | Richmond | CheckUpload | Pass | Pass |  | 100
S63839 | Richmond | InverterUptime | Pass | Pass |  | 100
S63839 | Richmond | NetworkCom | Pass | Pass | Pass: 100.00 % PowerManager 2200: 18 of 18 TCP devices communicating normally PowerManager 2200: 24 of 24 devices on port 1 communicating normally PowerManager 2200: 4 of 4 devices on port 4 communicating normally PowerManager 2200: 5 of 7 devices on port 0 communicating normally | 100
S63839 | Richmond | AlertRecipients | Pass | Pass |  | 100
S63839 | Richmond | CheckHW | Fail | Fail | Fail: 0.00 % 10 String INV's: Inverter group devices that don't receive data should be set to 'Offline'. 11 String INV's: Inverter group devices that don't receive data should be set to 'Offline'. | 0 | {'index': 0, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H465413', 'hardwareName': "10 String INV's", 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H465414', 'hardwareName': "11 String INV's", 'isAcknowledged': False}
S63839 | Richmond | CheckSysSize | Pass | Pass |  | 100
S63839 | Richmond | DefaultAlerts | Fail | Fail | AE Smart UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H401010', 'hardwareName': 'AE Smart UPS', 'isAcknowledged': False}
S63839 | Richmond | HasPVmodel | Pass | Pass |  | 100
S63839 | Richmond | HasWSmodel | Pass | Pass |  | 100
S63839 | Richmond | InvalidAlerts | Pass | Pass |  | 100
S63839 | Richmond | SiteConfig | Pass | Pass |  | 100
S63839 | Richmond | CheckMeterVoltage | Pass | Pass |  | 100
S63839 | Richmond | CheckWeather | Pass | Pass |  | 100
S63839 | Richmond | DataCuration | Pass | Pass |  | 100
S63839 | Richmond | kWandkWh | Pass | Pass |  | 100
S63839 | Richmond | PVPMenergy | Pass | Pass | ION 8650 Production Meter: Inverter / meter energy correlation: % | 95.4773
S63839 | Richmond | Tracker | Fail | Fail | Fail: 0.00 % NCU 1: Tracker ' Position A1 S 10 ' always 22.9354 degrees NCU 1: Tracker ' Position A1 S 56 ' always -21.2792 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 10\t' always \t\t\t 22.9354\t degrees", 'success': 0.0, 'hardwareKey': 'H401009', 'hardwareName': 'NCU 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 56\t' always \t\t\t -21.2792\t degrees", 'success': 0.0, 'hardwareKey': 'H401009', 'hardwareName': 'NCU 1', 'isAcknowledged': False}
S63839 | Richmond | CheckPMCTs | Pass | Pass | ION 8650 Production Meter: Phase current ratio 99.8774765643334 %, PF: 0.9984334821381202 | 99.8775
S63839 | Richmond | EnergyRatio | Fail | Fail | Inverter 24: High energy ratio: 1.1002364656703594 | 89.9764 | {'index': 0, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.1002364656703594\t', 'success': 0.8997635343296406, 'hardwareKey': 'H401001', 'hardwareName': 'Inverter 24', 'isAcknowledged': False}
S63839 | Richmond | ProductionEnergy | Pass | Pass |  | 100
S63839 | Richmond | PVlosses | Pass | Pass |  | 100
S63839 | Richmond | PVmodelEnergy24 | Pass | Pass |  | 102.0256
S63839 | Richmond | CorrectiveAction | Fail | Fail | Equipment repair required. Low availability , Inverter group : 10 String INV's, 11 String INV's | 50 | {'index': 0, 'result': 3, 'detail': "Equipment repair required. \t\t\t Low availability\t, \t\t\t Inverter group\t: \t\t\t 10 String INV's, 11 String INV's\t", 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S63840 | Upson | Availability | Pass | Pass |  | 100
S63840 | Upson | CheckUpload | Pass | Pass |  | 100
S63840 | Upson | InverterUptime | Pass | Pass |  | 100
S63840 | Upson | NetworkCom | Pass | Pass | Pass: 100.00 % PowerManager 2200: 18 of 18 TCP devices communicating normally PowerManager 2200: 24 of 24 devices on port 1 communicating normally PowerManager 2200: 4 of 4 devices on port 4 communicating normally | 100
S63840 | Upson | AlertRecipients | Pass | Pass |  | 100
S63840 | Upson | CheckHW | Pass | Pass |  | 100
S63840 | Upson | CheckSysSize | Pass | Pass |  | 100
S63840 | Upson | DefaultAlerts | Fail | Fail | AE Smart UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H401086', 'hardwareName': 'AE Smart UPS', 'isAcknowledged': False}
S63840 | Upson | HasPVmodel | Pass | Pass |  | 100
S63840 | Upson | HasWSmodel | Pass | Pass |  | 100
S63840 | Upson | InvalidAlerts | Pass | Pass |  | 100
S63840 | Upson | SiteConfig | Pass | Pass |  | 100
S63840 | Upson | CheckMeterVoltage | Pass | Pass |  | 100
S63840 | Upson | CheckWeather | Fail | Fail | Fail: 0.00 % Kipp & Zonen SMP-12 (BPOA) - PY2: Insolation low, : < Kipp & Zonen SMP-12 (GHI) - PY1: Insolation mismatch 99.78298766698934 %, check azimuth/tilt settings: Sun (GHI Temp comp) (this is a secondary sensor) Kipp & Zonen SMP-12 (POA) - PY0: Insolation mismatch + 60.68311884422632 % (higher than other sensors), check azimuth/tilt settings: Sun (POA Temp comp) Kipp & Zonen SMP-12 (BPOA) - PY2: Insolation mismatch -88.41021858382322 %, check azimuth/tilt settings: Sun (POA Temp comp) (this is a secondary sensor) | 0 | {'index': 0, 'result': 3, 'detail': 'Insolation low, : < ', 'success': 0.0, 'hardwareKey': 'H401082', 'hardwareName': 'Kipp & Zonen SMP-12 (BPOA) - PY2', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Insolation mismatch +\t\t\t 60.68311884422632\t % (higher than other sensors), check azimuth/tilt settings: \t\t\t Sun (POA Temp comp)\t', 'success': 0.0, 'hardwareKey': 'H401080', 'hardwareName': 'Kipp & Zonen SMP-12 (POA) - PY0', 'isAcknowledged': False}
S63840 | Upson | DataCuration | Pass | Pass |  | 100
S63840 | Upson | kWandkWh | Pass | Pass |  | 100
S63840 | Upson | PVPMenergy | Pass | Pass | ION 8650 Production Meter: Inverter / meter energy correlation: % | 98.7121
S63840 | Upson | Tracker | Pass | Pass |  | 100
S63840 | Upson | CheckPMCTs | Fail | Fail | ION 8650 Production Meter: Phase current ratio 99.8591811126853 %, PF: 6.123031769111886E-17 | 99.8592 | {'index': 0, 'result': 3, 'detail': 'Phase current ratio \t\t\t 99.8591811126853\t %, PF: \t\t\t 6.123031769111886E-17\t', 'success': 0.998591811126853, 'hardwareKey': 'H401051', 'hardwareName': 'ION 8650 Production Meter', 'isAcknowledged': False}
S63840 | Upson | EnergyRatio | Pass | Pass |  | 95.4416
S63840 | Upson | ProductionEnergy | Pass | Pass |  | 100
S63840 | Upson | PVlosses | Pass | Pass |  | 100
S63840 | Upson | PVmodelEnergy24 | Pass | Pass |  | 101.7875
S63840 | Upson | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S64602 | McLean | Availability | Fail | Fail | PYRANOMETER - BPOA (PY2): Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H421855', 'hardwareName': 'PYRANOMETER - BPOA (PY2)', 'isAcknowledged': False}
S64602 | McLean | CheckUpload | Fail | Fail | PYRANOMETER - BPOA (PY2): Last upload: 6/16/2025 9:05 PM ( US/Eastern ), delay: 356 d 13.5 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 6/16/2025 9:05 PM\t (\t\t\t US/Eastern\t), delay: \t\t\t 356 d 13.5 h\t', 'success': 0.0, 'hardwareKey': 'H421855', 'hardwareName': 'PYRANOMETER - BPOA (PY2)', 'isAcknowledged': False}
S64602 | McLean | InverterUptime | Pass | Pass |  | 100
S64602 | McLean | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 28 of 28 TCP devices communicating normally DATALOGGER: 20 of 20 devices on port 1 communicating normally DATALOGGER: 4 of 5 devices on port 3 communicating normally | 100
S64602 | McLean | AlertRecipients | Pass | Pass |  | 100
S64602 | McLean | CheckHW | Fail | Fail | TRACKER CONTROL (ST0): Multiple devices on : | 0 | {'index': 0, 'result': 3, 'detail': 'Multiple devices on : ', 'success': 0.0, 'hardwareKey': 'H421859', 'hardwareName': 'TRACKER CONTROL (ST0)', 'isAcknowledged': False}
S64602 | McLean | CheckSysSize | Pass | Pass |  | 100
S64602 | McLean | DefaultAlerts | Fail | Fail | Fail: 0.00 % TRACKER CONTROL (ST0): Default alerts not set: 974 UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 974\t', 'success': 0.0, 'hardwareKey': 'H421860', 'hardwareName': 'TRACKER CONTROL (ST0)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H421862', 'hardwareName': 'UPS', 'isAcknowledged': False}
S64602 | McLean | HasPVmodel | Pass | Pass |  | 100
S64602 | McLean | HasWSmodel | Pass | Pass |  | 100
S64602 | McLean | InvalidAlerts | Fail | Fail | TRACKER CONTROL (ST0): Alerts not valid: 526,649,696 | 0 | {'index': 0, 'result': 3, 'detail': 'Alerts not valid: \t\t\t 526,649,696\t', 'success': 0.0, 'hardwareKey': 'H421860', 'hardwareName': 'TRACKER CONTROL (ST0)', 'isAcknowledged': False}
S64602 | McLean | SiteConfig | Pass | Pass |  | 100
S64602 | McLean | CheckMeterVoltage | Pass | Pass |  | 100
S64602 | McLean | CheckWeather | Pass | Pass |  | 100
S64602 | McLean | DataCuration | Pass | Pass |  | 100
S64602 | McLean | kWandkWh | Pass | Pass |  | 100
S64602 | McLean | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 98.1527
S64602 | McLean | Tracker | Fail | Fail | Fail: 0.00 % TRACKER CONTROL (ST0): Tracker ' Position A1 S 16 ' always 0 degrees TRACKER CONTROL (ST0): Tracker ' Position A1 S 48 ' always 0 degrees TRACKER CONTROL (ST0): Tracker ' Position A1 S 50 ' always 0 degrees TRACKER CONTROL (ST0): Tracker ' Position A1 S 57 ' always 0 degrees TRACKER CONTROL (ST0): Tracker ' Position A1 S 76 ' always 0 degrees TRACKER CONTROL (ST0): Tracker ' Position A1 S 122 ' always 0 degrees TRACKER CONTROL (ST0): Tracker ' Position A1 S 127 ' always 0 degrees TRACKER CONTROL (ST0): Tracker ' Position A1 S 144 ' always 0 degrees TRACKER CONTROL (ST0): Average tracker error ( Position A1 S 9 ): 40.63263 degrees TRACKER CONTROL (ST0): Average tracker error ( Position A1 S 10 ): 24.13425 degrees TRACKER CONTROL (ST0): Average tracker error ( Position A1 S 23 ): 60.5247 degrees TRACKER CONTROL (ST0): Average tracker error ( Position A1 S 31 ): 24.13637 degrees TRACKER CONTROL (ST0): Average tracker error ( Position A1 S 51 ): 35.03534 degrees TRACKER CONTROL (ST0): Average tracker error ( Position A1 S 63 ): 23.98062 degrees TRACKER CONTROL (ST0): Average tracker error ( Position A1 S 81 ): 23.98043 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 16\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H421859', 'hardwareName': 'TRACKER CONTROL (ST0)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 48\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H421859', 'hardwareName': 'TRACKER CONTROL (ST0)', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 50\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H421859', 'hardwareName': 'TRACKER CONTROL (ST0)', 'isAcknowledged': False}
S64602 | McLean | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.1830850552619 %, PF: 0.980000003315249 | 99.1831
S64602 | McLean | EnergyRatio | Pass | Pass |  | 80.4214
S64602 | McLean | ProductionEnergy | Pass | Pass |  | 100
S64602 | McLean | PVlosses | Fail | Fail | Fail: 0.00 % INVERTER 4: Excessive soiling loss: 5.254431091189658 % ( 61.483518786 kWh) INVERTER 10: Excessive soiling loss: 8.50190911536207 % ( 99.483137135 kWh) INVERTER 20: Excessive soiling loss: 6.227783763105084 % ( 67.00463552199999 kWh) INVERTER 28: Excessive soiling loss: 5.501322125479176 % ( 59.21267723500001 kWh) INVERTER 29: Excessive soiling loss: 5.590141676976005 % ( 65.41175911300002 kWh) METER - PRODUCTION: Excessive soiling loss: 7.64901 % ( 3648.2161351444092 kWh) | 0 | {'index': 0, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 5.254431091189658\t % (\t\t\t 61.483518786\t kWh)', 'success': 0.0, 'hardwareKey': 'H421816', 'hardwareName': 'INVERTER 4', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 8.50190911536207\t % (\t\t\t 99.483137135\t kWh)', 'success': 0.0, 'hardwareKey': 'H421822', 'hardwareName': 'INVERTER 10', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 6.227783763105084\t % (\t\t\t 67.00463552199999\t kWh)', 'success': 0.0, 'hardwareKey': 'H421832', 'hardwareName': 'INVERTER 20', 'isAcknowledged': False}
S64602 | McLean | PVmodelEnergy24 | Pass | Pass |  | 93.399
S64602 | McLean | CorrectiveAction | Fail | Fail | Fail: 0.00 % PV module soiling loss is kWh/day, but cleaning is not required because rain is forecast. Equipment repair required. Low availability , Weather station : PYRANOMETER - BPOA (PY2) | 0 | {'index': 0, 'result': 3, 'detail': 'PV module soiling loss is kWh/day, but cleaning is not required because rain is forecast. ', 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Low availability\t, \t\t\t Weather station\t: \t\t\t PYRANOMETER - BPOA (PY2)\t', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S64603 | Shorthorn | Availability | Fail | Fail | Fail: 0.00 % TRACKER CONTROL (ST1): Availability: 54.736842105263165 % 12 String INV's: Availability: 0 % 13 String INV's: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 54.736842105263165\t %', 'success': 0.0, 'hardwareKey': 'H422145', 'hardwareName': 'TRACKER CONTROL (ST1)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H595430', 'hardwareName': "12 String INV's", 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H595436', 'hardwareName': "13 String INV's", 'isAcknowledged': False}
S64603 | Shorthorn | CheckUpload | Fail | Fail | TRACKER CONTROL (ST1): Last upload: 6/8/2026 8:56 AM ( US/Eastern ), delay: 10.3 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 6/8/2026 8:56 AM\t (\t\t\t US/Eastern\t), delay: \t\t\t 10.3 h\t', 'success': 0.0, 'hardwareKey': 'H422145', 'hardwareName': 'TRACKER CONTROL (ST1)', 'isAcknowledged': False}
S64603 | Shorthorn | InverterUptime | Pass | Pass |  | 100
S64603 | Shorthorn | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 57 of 58 TCP devices communicating normally DATALOGGER: 24 of 24 devices on port 1 communicating normally DATALOGGER: 2 of 2 devices on port 3 communicating normally DATALOGGER: 3 of 3 devices on port 4 communicating normally DATALOGGER: 57 of 60 devices on port 0 communicating normally | 100
S64603 | Shorthorn | AlertRecipients | Pass | Pass |  | 100
S64603 | Shorthorn | CheckHW | Fail | Fail | Fail: 0.00 % 12 String INV's: Inverter group devices that don't receive data should be set to 'Offline'. 13 String INV's: Inverter group devices that don't receive data should be set to 'Offline'. | 0 | {'index': 0, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H595430', 'hardwareName': "12 String INV's", 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H595436', 'hardwareName': "13 String INV's", 'isAcknowledged': False}
S64603 | Shorthorn | CheckSysSize | Pass | Pass |  | 100
S64603 | Shorthorn | DefaultAlerts | Fail | Fail | UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H422147', 'hardwareName': 'UPS', 'isAcknowledged': False}
S64603 | Shorthorn | HasPVmodel | Pass | Pass |  | 100
S64603 | Shorthorn | HasWSmodel | Pass | Pass |  | 100
S64603 | Shorthorn | InvalidAlerts | Pass | Pass |  | 100
S64603 | Shorthorn | SiteConfig | Pass | Pass |  | 100
S64603 | Shorthorn | CheckMeterVoltage | Pass | Pass |  | 100
S64603 | Shorthorn | CheckWeather | Pass | Pass |  | 100
S64603 | Shorthorn | DataCuration | Pass | Pass |  | 100
S64603 | Shorthorn | kWandkWh | Pass | Pass |  | 100
S64603 | Shorthorn | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 98.2716
S64603 | Shorthorn | Tracker | Fail | Fail | Fail: 0.00 % TRACKER CONTROL (ST0): Tracker ' Position A1 S 44 ' always 0 degrees TRACKER CONTROL (ST2): Tracker ' Position A1 S 77 ' always 0 degrees TRACKER CONTROL (ST2): Average tracker error ( Position A1 S 25 ): 33.88015 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 44\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H422144', 'hardwareName': 'TRACKER CONTROL (ST0)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 77\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H422146', 'hardwareName': 'TRACKER CONTROL (ST2)', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Average tracker error (\t\t\t Position A1 S 25\t): \t\t\t 33.88015\t degrees', 'success': 0.0, 'hardwareKey': 'H422146', 'hardwareName': 'TRACKER CONTROL (ST2)', 'isAcknowledged': False}
S64603 | Shorthorn | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 97.78703487158398 %, PF: 0.980000003315249 | 97.787
S64603 | Shorthorn | EnergyRatio | Pass | Pass |  | 92.4139
S64603 | Shorthorn | ProductionEnergy | Pass | Pass |  | 100
S64603 | Shorthorn | PVlosses | Pass | Pass |  | 100
S64603 | Shorthorn | PVmodelEnergy24 | Pass | Pass |  | 99.4199
S64603 | Shorthorn | CorrectiveAction | Fail | Fail | Equipment repair required. Low availability , Solar tracker, Inverter group : TRACKER CONTROL (ST1), 12 String INV's, 13 String INV's | 50 | {'index': 0, 'result': 3, 'detail': "Equipment repair required. \t\t\t Low availability\t, \t\t\t Solar tracker, Inverter group\t: \t\t\t TRACKER CONTROL (ST1), 12 String INV's, 13 String INV's\t", 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S65216 | Green Solar | Availability | Pass | Pass |  | 100
S65216 | Green Solar | CheckUpload | Pass | Pass |  | 100
S65216 | Green Solar | InverterUptime | Pass | Pass |  | 100
S65216 | Green Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 9 of 9 TCP devices communicating normally DATALOGGER: 4 of 4 devices on port 2 communicating normally DATALOGGER: 10 of 10 devices on port 0 communicating normally | 100
S65216 | Green Solar | AlertRecipients | Pass | Pass |  | 100
S65216 | Green Solar | CheckHW | Pass | Pass |  | 100
S65216 | Green Solar | CheckSysSize | Pass | Pass |  | 100
S65216 | Green Solar | DefaultAlerts | Pass | Pass |  | 100
S65216 | Green Solar | HasPVmodel | Pass | Pass |  | 100
S65216 | Green Solar | HasWSmodel | Pass | Pass |  | 100
S65216 | Green Solar | InvalidAlerts | Pass | Pass |  | 100
S65216 | Green Solar | SiteConfig | Pass | Pass |  | 100
S65216 | Green Solar | CheckMeterVoltage | Pass | Pass |  | 100
S65216 | Green Solar | CheckWeather | Pass | Pass |  | 100
S65216 | Green Solar | DataCuration | Pass | Pass |  | 100
S65216 | Green Solar | kWandkWh | Pass | Pass |  | 100
S65216 | Green Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 99.2579
S65216 | Green Solar | Tracker | Pass | Pass |  | 100
S65216 | Green Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.23426332441511 %, PF: 1 | 99.2343
S65216 | Green Solar | EnergyRatio | Pass | Pass |  | 98.5307
S65216 | Green Solar | ProductionEnergy | Pass | Pass |  | 100
S65216 | Green Solar | PVlosses | Pass | Pass |  | 100
S65216 | Green Solar | PVmodelEnergy24 | Pass | Pass |  | 98.5276
S65216 | Green Solar | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S65784 | Washington Solar | Availability | Fail | Fail | Fail: 0.00 % 13-String Inverters: Availability: 0 % 12-String Inverters: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H525393', 'hardwareName': '13-String Inverters', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H525822', 'hardwareName': '12-String Inverters', 'isAcknowledged': False}
S65784 | Washington Solar | CheckUpload | Pass | Pass |  | 100
S65784 | Washington Solar | InverterUptime | Pass | Pass |  | 100
S65784 | Washington Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 29 of 29 TCP devices communicating normally DATALOGGER: 40 of 40 devices on port 1 communicating normally DATALOGGER: 3 of 3 devices on port 4 communicating normally DATALOGGER: 1 of 1 devices on port 3 communicating normally DATALOGGER: 9 of 11 devices on port 0 communicating normally | 100
S65784 | Washington Solar | AlertRecipients | Pass | Pass |  | 100
S65784 | Washington Solar | CheckHW | Fail | Fail | Fail: 0.00 % 13-String Inverters: Inverter group devices that don't receive data should be set to 'Offline'. 12-String Inverters: Inverter group devices that don't receive data should be set to 'Offline'. | 0 | {'index': 0, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H525393', 'hardwareName': '13-String Inverters', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H525822', 'hardwareName': '12-String Inverters', 'isAcknowledged': False}
S65784 | Washington Solar | CheckSysSize | Pass | Pass |  | 100
S65784 | Washington Solar | DefaultAlerts | Fail | Fail | Fail: 0.00 % DIGITAL I/O - XFMR ALARMS: Default alerts not enabled: Transformer Monitor (534) ALSOENERGY SMART UPS: Default alerts not set: 250 AE Smart UPS -SO86824: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not enabled: \t\t\t Transformer Monitor (534)\t', 'success': 0.0, 'hardwareKey': 'H457099', 'hardwareName': 'DIGITAL I/O - XFMR ALARMS', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H457149', 'hardwareName': 'ALSOENERGY SMART UPS', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H473430', 'hardwareName': 'AE Smart UPS -SO86824', 'isAcknowledged': False}
S65784 | Washington Solar | HasPVmodel | Pass | Pass |  | 100
S65784 | Washington Solar | HasWSmodel | Pass | Pass |  | 100
S65784 | Washington Solar | InvalidAlerts | Pass | Pass |  | 100
S65784 | Washington Solar | SiteConfig | Pass | Pass |  | 100
S65784 | Washington Solar | CheckMeterVoltage | Pass | Pass |  | 100
S65784 | Washington Solar | CheckWeather | Pass | Pass |  | 100
S65784 | Washington Solar | DataCuration | Fail | Fail | Fail: 0.00 % INVERTER 1: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 1: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 1: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 2: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 2: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 2: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 3: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 3: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 3: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 4: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 4: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 4: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 5: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 5: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 5: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 6: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 6: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 6: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 7: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 7: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 7: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 8: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 8: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 8: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 9: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 9: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 9: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 10: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 10: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 10: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 11: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 11: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 11: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 12: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 12: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 12: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 13: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 13: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 13: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 14: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 14: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 14: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 15: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 15: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 15: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 16: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 16: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 16: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 17: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 17: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 17: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 18: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 18: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 18: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 19: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 19: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 19: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 20: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 20: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 20: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 21: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 21: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 21: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 22: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 22: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 22: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 23: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 23: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 23: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 24: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 24: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 24: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 25: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 25: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 25: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 26: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 26: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 26: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 27: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 27: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 27: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 28: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 28: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 28: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 29: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 29: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 29: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 30: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 30: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 30: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 31: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 31: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 31: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 32: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 32: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 32: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 33: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 33: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 33: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 34: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 34: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 34: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 35: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 35: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 35: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 36: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 36: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 36: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 37: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 37: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 37: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 38: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 38: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 38: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 39: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 39: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 39: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . INVERTER 40: The value " AC Voltage AN " ( VacA ) is stuck at 0 V . INVERTER 40: The value " AC Voltage BN " ( VacB ) is stuck at 0 V . INVERTER 40: The value " AC Voltage CN " ( VacC ) is stuck at 0 V . | 0 | {'index': 0, 'result': 3, 'detail': 'The value "\t\t\t AC Voltage AN\t" (\t\t\t VacA\t) is stuck at \t\t\t 0\t \t\t\t V\t.', 'success': 0.0, 'hardwareKey': 'H457102', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'The value "\t\t\t AC Voltage BN\t" (\t\t\t VacB\t) is stuck at \t\t\t 0\t \t\t\t V\t.', 'success': 0.0, 'hardwareKey': 'H457102', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'The value "\t\t\t AC Voltage CN\t" (\t\t\t VacC\t) is stuck at \t\t\t 0\t \t\t\t V\t.', 'success': 0.0, 'hardwareKey': 'H457102', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}
S65784 | Washington Solar | kWandkWh | Pass | Pass |  | 100
S65784 | Washington Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 98.3686
S65784 | Washington Solar | Tracker | Fail | Fail | Fail: 0.00 % TRACKER CONTROL 1: Tracker ' Tracker Position TCU 1 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 2 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 3 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 4 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 5 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 6 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 7 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 8 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 9 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 10 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 11 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 12 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 13 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 14 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 15 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 16 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 17 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 18 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 19 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 20 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 21 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 22 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 23 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 24 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 25 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 26 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 27 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 28 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 29 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 30 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 31 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 32 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 33 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 34 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 35 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 36 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 37 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 38 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 39 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 40 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 41 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 42 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 43 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 44 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 45 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 46 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 47 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 48 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 49 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 50 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 51 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 52 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 53 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 54 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 55 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 56 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 57 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 58 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 59 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 60 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 61 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 62 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 63 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 64 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 65 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 66 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 67 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 68 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 69 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 70 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 71 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 72 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 73 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 74 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 75 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 76 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 77 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 78 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 79 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 80 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 81 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 82 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 83 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 84 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 85 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 86 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 87 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 88 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 89 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 90 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 91 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 92 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 93 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 94 ' always 0 degrees TRACKER CONTROL 1: Tracker ' Tracker Position TCU 95 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 97 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 99 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 101 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 103 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 105 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 107 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 109 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 110 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Tracker Position TCU 111 ' always 0 degrees TRACKER CONTROL 2: Average tracker error ( Tracker Position TCU 96 ): 29.323415 degrees TRACKER CONTROL 2: Average tracker error ( Tracker Position TCU 98 ): 29.461225 degrees TRACKER CONTROL 2: Average tracker error ( Tracker Position TCU 100 ): 29.305600000000002 degrees TRACKER CONTROL 2: Average tracker error ( Tracker Position TCU 102 ): 29.024074999999996 degrees TRACKER CONTROL 2: Average tracker error ( Tracker Position TCU 104 ): 29.343154999999996 degrees TRACKER CONTROL 2: Average tracker error ( Tracker Position TCU 106 ): 29.366554999999998 degrees TRACKER CONTROL 2: Average tracker error ( Tracker Position TCU 108 ): 29.023944999999998 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 1\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H457147', 'hardwareName': 'TRACKER CONTROL 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 2\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H457147', 'hardwareName': 'TRACKER CONTROL 1', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 3\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H457147', 'hardwareName': 'TRACKER CONTROL 1', 'isAcknowledged': False}
S65784 | Washington Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 94.877809035126 %, PF: 0.980000003315249 | 94.8778
S65784 | Washington Solar | EnergyRatio | Fail | Fail | Fail: 0.00 % INVERTER 1: High energy ratio: 1.1457513611167116 INVERTER 2: High energy ratio: 1.148669233853002 INVERTER 3: High energy ratio: 1.1515871065892924 INVERTER 4: High energy ratio: 1.1269556709327209 INVERTER 6: High energy ratio: 1.1241890039828042 INVERTER 7: High energy ratio: 1.1297223378826375 INVERTER 8: High energy ratio: 1.1251112262994432 INVERTER 9: High energy ratio: 1.1260334486160821 INVERTER 10: High energy ratio: 1.1241890039828042 INVERTER 11: High energy ratio: 1.1223445593495265 INVERTER 12: High energy ratio: 1.1223445593495265 INVERTER 13: High energy ratio: 1.148669233853002 INVERTER 14: High energy ratio: 1.1447787368712814 INVERTER 15: High energy ratio: 1.117733447766332 INVERTER 16: High energy ratio: 1.1214223370328877 INVERTER 17: High energy ratio: 1.118655670082971 INVERTER 18: High energy ratio: 1.1214223370328877 INVERTER 19: High energy ratio: 1.10297789070011 INVERTER 20: High energy ratio: 1.1262988762081088 INVERTER 21: High energy ratio: 1.1140445584997765 INVERTER 22: High energy ratio: 1.118655670082971 INVERTER 23: High energy ratio: 1.1195778923996098 INVERTER 24: High energy ratio: 1.1195778923996098 INVERTER 25: High energy ratio: 1.1496418580984322 INVERTER 26: High energy ratio: 1.1428334883804212 INVERTER 27: High energy ratio: 1.1496418580984322 INVERTER 28: High energy ratio: 1.1467239853621418 INVERTER 29: High energy ratio: 1.1564502278164432 INVERTER 30: High energy ratio: 1.1457513611167116 INVERTER 31: High energy ratio: 1.1340798701715498 INVERTER 32: High energy ratio: 1.1506144823438622 INVERTER 33: High energy ratio: 1.1389429913987006 INVERTER 34: High energy ratio: 1.1331072459261198 INVERTER 35: High energy ratio: 1.1321346216806896 INVERTER 36: High energy ratio: 1.1340798701715498 INVERTER 37: High energy ratio: 1.1389429913987006 INVERTER 38: High energy ratio: 1.1360251186624102 INVERTER 39: High energy ratio: 1.1457513611167116 METER - PRODUCTION: High energy ratio: 1.111664661253701 | 0 | {'index': 0, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.1457513611167116\t', 'success': 0.0, 'hardwareKey': 'H457102', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.148669233853002\t', 'success': 0.0, 'hardwareKey': 'H457103', 'hardwareName': 'INVERTER 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.1515871065892924\t', 'success': 0.0, 'hardwareKey': 'H457104', 'hardwareName': 'INVERTER 3', 'isAcknowledged': False}
S65784 | Washington Solar | ProductionEnergy | Pass | Pass |  | 100
S65784 | Washington Solar | PVlosses | Pass | Pass |  | 100
S65784 | Washington Solar | PVmodelEnergy24 | Pass | Pass |  | 111.8637
S65784 | Washington Solar | CorrectiveAction | Fail | Fail | Equipment repair required. Low availability , Inverter group : 13-String Inverters, 12-String Inverters | 50 | {'index': 0, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Low availability\t, \t\t\t Inverter group\t: \t\t\t 13-String Inverters, 12-String Inverters\t', 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S65785 | Harding Solar | Availability | Fail | Fail | Fail: 0.00 % 13 String: Availability: 0 % 12 String: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H596631', 'hardwareName': '13 String', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H596632', 'hardwareName': '12 String', 'isAcknowledged': False}
S65785 | Harding Solar | CheckUpload | Pass | Pass |  | 100
S65785 | Harding Solar | InverterUptime | Pass | Pass |  | 100
S65785 | Harding Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 20 of 20 TCP devices communicating normally DATALOGGER: 12 of 12 devices on port 1 communicating normally DATALOGGER: 1 of 1 devices on port 4 communicating normally DATALOGGER: 1 of 1 devices on port 2 communicating normally DATALOGGER: 2 of 2 devices on port 3 communicating normally DATALOGGER: 20 of 22 devices on port 0 communicating normally | 100
S65785 | Harding Solar | AlertRecipients | Pass | Pass |  | 100
S65785 | Harding Solar | CheckHW | Fail | Fail | Fail: 0.00 % 13 String: Inverter group devices that don't receive data should be set to 'Offline'. 12 String: Inverter group devices that don't receive data should be set to 'Offline'. | 0 | {'index': 0, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H596631', 'hardwareName': '13 String', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H596632', 'hardwareName': '12 String', 'isAcknowledged': False}
S65785 | Harding Solar | CheckSysSize | Pass | Pass |  | 100
S65785 | Harding Solar | DefaultAlerts | Fail | Fail | ALSOENERGY SMART UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H462629', 'hardwareName': 'ALSOENERGY SMART UPS', 'isAcknowledged': False}
S65785 | Harding Solar | HasPVmodel | Pass | Pass |  | 100
S65785 | Harding Solar | HasWSmodel | Pass | Pass |  | 100
S65785 | Harding Solar | InvalidAlerts | Pass | Pass |  | 100
S65785 | Harding Solar | SiteConfig | Pass | Pass |  | 100
S65785 | Harding Solar | CheckMeterVoltage | Pass | Pass |  | 100
S65785 | Harding Solar | CheckWeather | Pass | Pass |  | 100
S65785 | Harding Solar | DataCuration | Pass | Pass |  | 100
S65785 | Harding Solar | kWandkWh | Pass | Pass |  | 100
S65785 | Harding Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 98.0601
S65785 | Harding Solar | Tracker | Fail | Fail | TRACKER CONTROL: Average tracker error ( Tracker Position TCU 87 ): 32.78622 degrees | 0 | {'index': 0, 'result': 3, 'detail': 'Average tracker error (\t\t\t Tracker Position TCU 87\t): \t\t\t 32.78622\t degrees', 'success': 0.0, 'hardwareKey': 'H462628', 'hardwareName': 'TRACKER CONTROL', 'isAcknowledged': False}
S65785 | Harding Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.34837567213764 %, PF: 0.9797788674087979 | 99.3484
S65785 | Harding Solar | EnergyRatio | Pass | Pass |  | 88.48
S65785 | Harding Solar | ProductionEnergy | Pass | Pass |  | 100
S65785 | Harding Solar | PVlosses | Fail | Fail | Fail: 0.00 % INVERTER 3: Excessive soiling loss: 10.781972696674641 % ( 137.5430236 kWh) INVERTER 8: Excessive soiling loss: 9.423631211693206 % ( 120.21498909447 kWh) INVERTER 17: Excessive soiling loss: 10.467734418839322 % ( 137.726325481 kWh) | 0 | {'index': 0, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 10.781972696674641\t % (\t\t\t 137.5430236\t kWh)', 'success': 0.0, 'hardwareKey': 'H462601', 'hardwareName': 'INVERTER 3', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 9.423631211693206\t % (\t\t\t 120.21498909447\t kWh)', 'success': 0.0, 'hardwareKey': 'H462606', 'hardwareName': 'INVERTER 8', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 10.467734418839322\t % (\t\t\t 137.726325481\t kWh)', 'success': 0.0, 'hardwareKey': 'H462615', 'hardwareName': 'INVERTER 17', 'isAcknowledged': False}
S65785 | Harding Solar | PVmodelEnergy24 | Pass | Pass |  | 89.8518
S65785 | Harding Solar | CorrectiveAction | Fail | Fail | Equipment repair required. Low availability , Inverter group : 13 String, 12 String | 50 | {'index': 0, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Low availability\t, \t\t\t Inverter group\t: \t\t\t 13 String, 12 String\t', 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S65786 | Whitehall Solar | Availability | Fail | Fail | Fail: 0.00 % INVERTER 1: Availability: 98.21428571428571 % INVERTER 3: Availability: 98.21428571428571 % INVERTER 6: Availability: 98.21428571428571 % INVERTER 11: Availability: 98.21428571428571 % INVERTER 15: Availability: 98.21428571428571 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 98.21428571428571\t %', 'success': 0.0, 'hardwareKey': 'H463299', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 98.21428571428571\t %', 'success': 0.0, 'hardwareKey': 'H463301', 'hardwareName': 'INVERTER 3', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Availability: \t\t\t 98.21428571428571\t %', 'success': 0.0, 'hardwareKey': 'H463304', 'hardwareName': 'INVERTER 6', 'isAcknowledged': False}
S65786 | Whitehall Solar | CheckUpload | Pass | Pass |  | 100
S65786 | Whitehall Solar | InverterUptime | Pass | Pass |  | 100
S65786 | Whitehall Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER - RMA16960/SO110212: 6 of 6 TCP devices communicating normally DATALOGGER - RMA16960/SO110212: 16 of 16 devices on port 1 communicating normally DATALOGGER - RMA16960/SO110212: 3 of 3 devices on port 4 communicating normally DATALOGGER - RMA16960/SO110212: 1 of 1 devices on port 3 communicating normally | 100
S65786 | Whitehall Solar | AlertRecipients | Pass | Pass |  | 100
S65786 | Whitehall Solar | CheckHW | Pass | Pass |  | 100
S65786 | Whitehall Solar | CheckSysSize | Pass | Pass |  | 100
S65786 | Whitehall Solar | DefaultAlerts | Fail | Fail | Fail: 0.00 % TRACKER CONTROL: Default alerts not set: 3635 ALSOENERGY SMART UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 3635\t', 'success': 0.0, 'hardwareKey': 'H463320', 'hardwareName': 'TRACKER CONTROL', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H463321', 'hardwareName': 'ALSOENERGY SMART UPS', 'isAcknowledged': False}
S65786 | Whitehall Solar | HasPVmodel | Pass | Pass |  | 100
S65786 | Whitehall Solar | HasWSmodel | Pass | Pass |  | 100
S65786 | Whitehall Solar | InvalidAlerts | Pass | Pass |  | 100
S65786 | Whitehall Solar | SiteConfig | Pass | Pass |  | 100
S65786 | Whitehall Solar | CheckMeterVoltage | Pass | Pass |  | 100
S65786 | Whitehall Solar | CheckWeather | Fail | Fail | WEATHER STATION: Module temperature should exceed ambient | 0 | {'index': 0, 'result': 3, 'detail': 'Module temperature should exceed ambient', 'success': 0.0, 'hardwareKey': 'H463315', 'hardwareName': 'WEATHER STATION', 'isAcknowledged': False}
S65786 | Whitehall Solar | DataCuration | Pass | Pass |  | 100
S65786 | Whitehall Solar | kWandkWh | Pass | Pass |  | 100
S65786 | Whitehall Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 97.1014
S65786 | Whitehall Solar | Tracker | Fail | Fail | TRACKER CONTROL: Tracker ' Tracker Position TCU 24 ' always 0 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 24\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H463320', 'hardwareName': 'TRACKER CONTROL', 'isAcknowledged': False}
S65786 | Whitehall Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.1035589224608 %, PF: 0.980000003315249 | 99.1036
S65786 | Whitehall Solar | EnergyRatio | Pass | Pass |  | 84.9827
S65786 | Whitehall Solar | ProductionEnergy | Pass | Pass |  | 100
S65786 | Whitehall Solar | PVlosses | Pass | Pass |  | 100
S65786 | Whitehall Solar | PVmodelEnergy24 | Pass | Pass |  | 89.2944
S65786 | Whitehall Solar | CorrectiveAction | Pass | Pass | Slight losses or device availability issues should be addressed during the next scheduled maintenance activity. | 95
S65787 | Sunflower Solar | Availability | Pass | Pass |  | 100
S65787 | Sunflower Solar | CheckUpload | Pass | Pass |  | 100
S65787 | Sunflower Solar | InverterUptime | Pass | Pass |  | 100
S65787 | Sunflower Solar | NetworkCom | Pass | Pass | Pass: 100.00 % PM2200-RMA17561: 73 of 73 TCP devices communicating normally PM2200-RMA17561: 20 of 20 devices on port 1 communicating normally PM2200-RMA17561: 2 of 2 devices on port 4 communicating normally PM2200-RMA17561: 2 of 2 devices on port 2 communicating normally | 100
S65787 | Sunflower Solar | AlertRecipients | Pass | Pass |  | 100
S65787 | Sunflower Solar | CheckHW | Pass | Pass |  | 100
S65787 | Sunflower Solar | CheckSysSize | Pass | Pass |  | 100
S65787 | Sunflower Solar | DefaultAlerts | Fail | Fail | Fail: 0.00 % ALSOENERGY SMART UPS0: Default alerts not set: 250 ALSOENERGY SMART UPS1: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H458595', 'hardwareName': 'ALSOENERGY SMART UPS0', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H458596', 'hardwareName': 'ALSOENERGY SMART UPS1', 'isAcknowledged': False}
S65787 | Sunflower Solar | HasPVmodel | Pass | Pass |  | 100
S65787 | Sunflower Solar | HasWSmodel | Pass | Pass |  | 100
S65787 | Sunflower Solar | InvalidAlerts | Pass | Pass |  | 100
S65787 | Sunflower Solar | SiteConfig | Pass | Pass |  | 100
S65787 | Sunflower Solar | CheckMeterVoltage | Pass | Pass |  | 100
S65787 | Sunflower Solar | CheckWeather | Fail | Fail | Fail: 0.00 % PYRANOMETER - GHI (PY0): Insolation mismatch 99.94238769588361 %, check azimuth/tilt settings: Sun (GHI Temp comp) (this is a secondary sensor) PYRANOMETER - POA (PY1): Insolation mismatch + 71.5072766053518 % (higher than other sensors), check azimuth/tilt settings: Sun (POA Temp comp) PYRANOMETER - BPOA (PY2): Insolation mismatch -92.00909570559118 %, check azimuth/tilt settings: Sun (POA Temp comp) (this is a secondary sensor) | 0 | {'index': 0, 'result': 3, 'detail': 'Insolation mismatch +\t\t\t 71.5072766053518\t % (higher than other sensors), check azimuth/tilt settings: \t\t\t Sun (POA Temp comp)\t', 'success': 0.0, 'hardwareKey': 'H458588', 'hardwareName': 'PYRANOMETER - POA (PY1)', 'isAcknowledged': False}
S65787 | Sunflower Solar | DataCuration | Pass | Pass |  | 100
S65787 | Sunflower Solar | kWandkWh | Pass | Pass |  | 100
S65787 | Sunflower Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 98.4337
S65787 | Sunflower Solar | Tracker | Fail | Fail | Fail: 0.00 % TRACKER CONTROL (ST0): Tracker ' Tracker Position TCU 39 ' always 0 degrees TRACKER CONTROL (ST1): Tracker ' Tracker Position TCU 72 ' always 0 degrees TRACKER CONTROL (ST1): Tracker ' Tracker Position TCU 161 ' always 0 degrees TRACKER CONTROL (ST1): Tracker ' Tracker Position TCU 172 ' always 0 degrees TRACKER CONTROL (ST2): Tracker ' Tracker Position TCU 6 ' always 0 degrees TRACKER CONTROL (ST2): Tracker ' Tracker Position TCU 16 ' always 0 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 1 ): 10.4751725 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 2 ): 21.20052 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 3 ): 10.2321505 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 4 ): 7.1222235000000005 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 5 ): 13.5273755 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 6 ): 11.05734 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 7 ): 12.221969999999999 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 8 ): 9.0491105 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 9 ): 13.308567499999999 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 10 ): 12.162067 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 11 ): 9.865859 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 12 ): 8.647019 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 13 ): 7.7030805 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 14 ): 6.167068 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 15 ): 8.483488 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 16 ): 6.167579 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 17 ): 39.01155 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 18 ): 11.807537499999999 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 21 ): 16.652985 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 22 ): 5.766392 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 23 ): 5.100188500000001 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 24 ): 11.911414 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 29 ): 9.5069805 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 92 ): 16.234026 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 93 ): 21.939565 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 94 ): 21.738145000000003 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 95 ): 10.195254 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 96 ): 9.008851 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 97 ): 7.039002999999999 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 98 ): 7.1813839999999995 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 99 ): 9.271953499999999 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 100 ): 5.344596 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 101 ): 9.860597 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 102 ): 5.926126 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 103 ): 5.3845565 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 108 ): 6.8284234999999995 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 110 ): 6.469592 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 111 ): 6.4534175 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 121 ): 5.5230295 degrees TRACKER CONTROL (ST1): Average tracker error ( Tracker Position TCU 154 ): 8.37558 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 39\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H458592', 'hardwareName': 'TRACKER CONTROL (ST0)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 72\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H458593', 'hardwareName': 'TRACKER CONTROL (ST1)', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 161\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H498771', 'hardwareName': 'TRACKER CONTROL (ST1)', 'isAcknowledged': False}
S65787 | Sunflower Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.27007299270076 %, PF: 0.980000003315249 | 99.2701
S65787 | Sunflower Solar | EnergyRatio | Fail | Fail | Fail: 0.00 % INVERTER 1: High energy ratio: 1.8021736919211284 INVERTER 2: High energy ratio: 1.8021736919211284 INVERTER 3: High energy ratio: 1.8614232379568916 INVERTER 4: High energy ratio: 1.8350901063854412 INVERTER 5: High energy ratio: 1.863069058680107 INVERTER 6: High energy ratio: 1.8531941343408131 INVERTER 7: High energy ratio: 1.8597774172336758 INVERTER 8: High energy ratio: 1.8367359271086567 INVERTER 9: High energy ratio: 1.8548399550640289 INVERTER 10: High energy ratio: 1.8647148794033228 INVERTER 11: High energy ratio: 1.8433192100015194 INVERTER 12: High energy ratio: 1.8235693613229318 INVERTER 13: High energy ratio: 1.83179846493901 INVERTER 14: High energy ratio: 1.816986078430069 INVERTER 15: High energy ratio: 1.8548399550640289 INVERTER 16: High energy ratio: 1.8564857757872446 INVERTER 17: High energy ratio: 1.8581315965104601 INVERTER 18: High energy ratio: 1.8712981622961853 INVERTER 19: High energy ratio: 1.8531941343408131 INVERTER 20: High energy ratio: 1.7972362297514815 INVERTER 21: High energy ratio: 1.7445699666085808 INVERTER 22: High energy ratio: 1.739632504438934 INVERTER 23: High energy ratio: 1.66557057189423 INVERTER 24: High energy ratio: 1.7083619106978367 INVERTER 25: High energy ratio: 1.7314034008228558 INVERTER 26: High energy ratio: 1.734695042269287 INVERTER 27: High energy ratio: 1.7314034008228558 INVERTER 28: High energy ratio: 1.7314034008228558 INVERTER 29: High energy ratio: 1.7281117593764244 INVERTER 30: High energy ratio: 1.7149451935906994 INVERTER 31: High energy ratio: 1.7001328070817585 INVERTER 32: High energy ratio: 1.7017786278049742 INVERTER 33: High energy ratio: 1.7281117593764244 INVERTER 34: High energy ratio: 1.8334442856622255 INVERTER 35: High energy ratio: 1.8005278711979127 INVERTER 36: High energy ratio: 1.7840696639657563 INVERTER 37: High energy ratio: 1.775840560349678 INVERTER 38: High energy ratio: 1.7692572774568156 INVERTER 39: High energy ratio: 1.688612062019249 INVERTER 40: High energy ratio: 1.7791322017961093 INVERTER 41: High energy ratio: 1.7001328070817585 INVERTER 42: High energy ratio: 1.798882050474697 INVERTER 43: High energy ratio: 1.7149451935906994 INVERTER 44: High energy ratio: 1.711653552144268 INVERTER 45: High energy ratio: 1.7182368350371306 INVERTER 46: High energy ratio: 1.6984869863585428 INVERTER 47: High energy ratio: 1.7906529468586188 INVERTER 48: High energy ratio: 1.7791322017961093 INVERTER 49: High energy ratio: 1.7791322017961093 INVERTER 50: High energy ratio: 1.780778022519325 INVERTER 51: High energy ratio: 1.785715484688972 INVERTER 52: High energy ratio: 1.7593823531175217 INVERTER 53: High energy ratio: 1.7643198152871686 INVERTER 54: High energy ratio: 1.7659656360103841 INVERTER 55: High energy ratio: 1.7248201179299931 INVERTER 56: High energy ratio: 1.7741947396264623 INVERTER 57: High energy ratio: 1.7363408629925026 INVERTER 58: High energy ratio: 1.7610281738407374 INVERTER 59: High energy ratio: 1.7610281738407374 INVERTER 60: High energy ratio: 1.7676114567335999 INVERTER 61: High energy ratio: 1.675445496233524 INVERTER 62: High energy ratio: 1.7741947396264623 INVERTER 63: High energy ratio: 1.7840696639657563 INVERTER 64: High energy ratio: 1.7824238432425406 INVERTER 65: High energy ratio: 1.7939445883050502 INVERTER 66: High energy ratio: 1.844965030724735 INVERTER 67: High energy ratio: 1.8548399550640289 INVERTER 68: High energy ratio: 1.8515483136175976 INVERTER 69: High energy ratio: 1.8597774172336758 INVERTER 70: High energy ratio: 1.8466108514479507 INVERTER 71: High energy ratio: 1.7791322017961093 INVERTER 72: High energy ratio: 1.680242742638858 INVERTER 73: High energy ratio: 1.868006520849754 INVERTER 74: High energy ratio: 1.8383817478318725 INVERTER 75: High energy ratio: 1.8712981622961853 INVERTER 76: High energy ratio: 1.8581315965104601 INVERTER 77: High energy ratio: 1.8515483136175976 INVERTER 78: High energy ratio: 1.8005278711979127 INVERTER 79: High energy ratio: 1.7955904090282657 INVERTER 80: High energy ratio: 1.7972362297514815 METER - PRODUCTION: High energy ratio: 1.7563799506911597 | 0 | {'index': 0, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.8021736919211284\t', 'success': 0.0, 'hardwareKey': 'H458507', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.8021736919211284\t', 'success': 0.0, 'hardwareKey': 'H458508', 'hardwareName': 'INVERTER 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.8614232379568916\t', 'success': 0.0, 'hardwareKey': 'H458509', 'hardwareName': 'INVERTER 3', 'isAcknowledged': False}
S65787 | Sunflower Solar | ProductionEnergy | Pass | Pass |  | 100
S65787 | Sunflower Solar | PVlosses | Pass | Pass |  | 100
S65787 | Sunflower Solar | PVmodelEnergy24 | Fail | Fail | Energy above expected ( 175.61938332465746 %) | 175.6194 | {'index': 0, 'result': 3, 'detail': 'Energy above expected (\t\t\t 175.61938332465746\t %)', 'success': 1.7561938332465747, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S65787 | Sunflower Solar | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S65788 | Gray Fox Solar | Availability | Fail | Fail | INVERTER 2.6: Availability: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H458213', 'hardwareName': 'INVERTER 2.6', 'isAcknowledged': False}
S65788 | Gray Fox Solar | CheckUpload | Fail | Fail | INVERTER 2.6: Last upload: 5/20/2026 6:17 PM ( US/Eastern ), delay: 11 d 7.7 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 5/20/2026 6:17 PM\t (\t\t\t US/Eastern\t), delay: \t\t\t 11 d 7.7 h\t', 'success': 0.0, 'hardwareKey': 'H458213', 'hardwareName': 'INVERTER 2.6', 'isAcknowledged': False}
S65788 | Gray Fox Solar | InverterUptime | Fail | Fail | Fail: 0.00 % 12 String Inverters: Inverter uptime: 95.2380952380952 % 1 of 40 inverters failed to achieve an uptime of 100 % | 0 | {'index': 0, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 95.2380952380952\t %', 'success': 0.0, 'hardwareKey': 'H604347', 'hardwareName': '12 String Inverters', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': '\t\t\t 1\t of \t\t\t 40\t inverters failed to achieve an uptime of \t\t\t 100\t %', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S65788 | Gray Fox Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 27 of 28 TCP devices communicating normally DATALOGGER: 20 of 20 devices on port 1 communicating normally DATALOGGER: 4 of 4 devices on port 3 communicating normally | 100
S65788 | Gray Fox Solar | AlertRecipients | Pass | Pass |  | 100
S65788 | Gray Fox Solar | CheckHW | Pass | Pass |  | 100
S65788 | Gray Fox Solar | CheckSysSize | Pass | Pass |  | 100
S65788 | Gray Fox Solar | DefaultAlerts | Fail | Fail | ALSOENERGY SMART UPS: Default alerts not set: 250 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 250\t', 'success': 0.0, 'hardwareKey': 'H458234', 'hardwareName': 'ALSOENERGY SMART UPS', 'isAcknowledged': False}
S65788 | Gray Fox Solar | HasPVmodel | Pass | Pass |  | 100
S65788 | Gray Fox Solar | HasWSmodel | Pass | Pass |  | 100
S65788 | Gray Fox Solar | InvalidAlerts | Pass | Pass |  | 100
S65788 | Gray Fox Solar | SiteConfig | Pass | Pass |  | 100
S65788 | Gray Fox Solar | CheckMeterVoltage | Pass | Pass |  | 100
S65788 | Gray Fox Solar | CheckWeather | Pass | Pass |  | 100
S65788 | Gray Fox Solar | DataCuration | Pass | Pass |  | 100
S65788 | Gray Fox Solar | kWandkWh | Pass | Pass |  | 100
S65788 | Gray Fox Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 98.5459
S65788 | Gray Fox Solar | Tracker | Fail | Fail | Fail: 0.00 % TRACKER CONTROL: Tracker ' Tracker Position TCU 49 ' always 0 degrees TRACKER CONTROL: Tracker ' Tracker Position TCU 131 ' always 0 degrees TRACKER CONTROL: Tracker ' Tracker Position TCU 153 ' always 0 degrees TRACKER CONTROL: Average tracker error ( Tracker Position TCU 1 ): 10.3144 degrees TRACKER CONTROL: Average tracker error ( Tracker Position TCU 4 ): 12.1656 degrees TRACKER CONTROL: Average tracker error ( Tracker Position TCU 5 ): 6.880263 degrees TRACKER CONTROL: Average tracker error ( Tracker Position TCU 7 ): 8.897565 degrees TRACKER CONTROL: Average tracker error ( Tracker Position TCU 77 ): 6.202817 degrees TRACKER CONTROL: Average tracker error ( Tracker Position TCU 78 ): 6.671819 degrees TRACKER CONTROL: Average tracker error ( Tracker Position TCU 151 ): 9.488167 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 49\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H458233', 'hardwareName': 'TRACKER CONTROL', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 131\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H496288', 'hardwareName': 'TRACKER CONTROL', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position TCU 153\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H496288', 'hardwareName': 'TRACKER CONTROL', 'isAcknowledged': False}
S65788 | Gray Fox Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.7351566434261 %, PF: 0.980000003315249 | 99.7352
S65788 | Gray Fox Solar | EnergyRatio | Pass | Pass |  | 88.5278
S65788 | Gray Fox Solar | ProductionEnergy | Pass | Pass |  | 100
S65788 | Gray Fox Solar | PVlosses | Fail | Fail | INVERTER 2.6: Downtime loss detected: 99.87916478813777 % ( 1146.5503340000002 kWh) | 0 | {'index': 0, 'result': 3, 'detail': 'Downtime loss detected: \t\t\t 99.87916478813777\t % (\t\t\t 1146.5503340000002\t kWh)', 'success': 0.0, 'hardwareKey': 'H458213', 'hardwareName': 'INVERTER 2.6', 'isAcknowledged': False}
S65788 | Gray Fox Solar | PVmodelEnergy24 | Pass | Pass |  | 88.6793
S65788 | Gray Fox Solar | CorrectiveAction | Fail | Fail | Corrective action recommended, ( kWh/day loss). | 50 | {'index': 0, 'result': 3, 'detail': 'Corrective action recommended, ( kWh/day loss). ', 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S65918 | C & B Graham Energy | Availability | Fail | Fail | Fail: 0.00 % METER - PRODUCTION 1: Availability: 0 % WEATHER STATION: Availability: 0 % PYRANOMETER - POA: Availability: 0 % PYRANOMETER - GHI: Availability: 0 % PYRANOMETER - BPOA: Availability: 0 % Availability, all inverters: 0 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H449718', 'hardwareName': 'METER - PRODUCTION 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H449758', 'hardwareName': 'WEATHER STATION', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H449759', 'hardwareName': 'PYRANOMETER - POA', 'isAcknowledged': False}
S65918 | C & B Graham Energy | CheckUpload | Fail | Fail | Fail: 0.00 % METER - PRODUCTION 1: Last upload: 4/27/2026 4:11 PM ( US/Eastern ), delay: 41 d 21.6 h INVERTER 7: Last upload: 6/2/2026 3:17 PM ( US/Eastern ), delay: 5 d 22.5 h INVERTER 8: Last upload: 6/8/2026 6:40 AM ( US/Eastern ), delay: 7.1 h INVERTER 9: Last upload: 6/2/2026 10:20 AM ( US/Eastern ), delay: 6 d 3.5 h INVERTER 10: Last upload: 6/8/2026 6:42 AM ( US/Eastern ), delay: 7.1 h INVERTER 13: Last upload: 5/21/2026 10:58 AM ( US/Eastern ), delay: 18 d 2.8 h INVERTER 17: Last upload: 4/22/2026 1:37 PM ( US/Eastern ), delay: 47 d 0.2 h INVERTER 23: Last upload: 4/10/2026 10:13 AM ( US/Eastern ), delay: 59 d 3.6 h INVERTER 34: Last upload: 6/1/2026 10:03 AM ( US/Eastern ), delay: 7 d 3.7 h INVERTER 35: Last upload: 4/6/2026 11:53 AM ( US/Eastern ), delay: 63 d 1.9 h WEATHER STATION: Last upload: 4/27/2026 4:11 PM ( US/Eastern ), delay: 41 d 21.6 h PYRANOMETER - POA: Last upload: 4/27/2026 4:10 PM ( US/Eastern ), delay: 41 d 21.6 h PYRANOMETER - GHI: Last upload: 6/2/2026 3:05 PM ( US/Eastern ), delay: 5 d 22.7 h PYRANOMETER - BPOA: Last upload: 4/27/2026 4:13 PM ( US/Eastern ), delay: 41 d 21.6 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 4/27/2026 4:11 PM\t (\t\t\t US/Eastern\t), delay: \t\t\t 41 d 21.6 h\t', 'success': 0.0, 'hardwareKey': 'H449718', 'hardwareName': 'METER - PRODUCTION 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Last upload: \t\t\t 6/2/2026 3:17 PM\t (\t\t\t US/Eastern\t), delay: \t\t\t 5 d 22.5 h\t', 'success': 0.0, 'hardwareKey': 'H449729', 'hardwareName': 'INVERTER 7', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Last upload: \t\t\t 6/8/2026 6:40 AM\t (\t\t\t US/Eastern\t), delay: \t\t\t 7.1 h\t', 'success': 0.0, 'hardwareKey': 'H449730', 'hardwareName': 'INVERTER 8', 'isAcknowledged': False}
S65918 | C & B Graham Energy | NetworkCom | Fail | Fail | Fail: 0.00 % PowerManager 2200 (SO101968): 34 of 43 TCP devices communicating normally PowerManager 2200 (SO101968): All connected devices on port 4 not communicating - likely local communication network failure PowerManager 2200 (SO101968): 0 of 1 devices on port 3 communicating normally | 0 | {'index': 0, 'result': 3, 'detail': 'All connected devices on port \t\t\t 4\t not communicating - likely local communication network failure', 'success': 0.0, 'hardwareKey': 'H527423', 'hardwareName': 'PowerManager 2200 (SO101968)', 'isAcknowledged': False}
S65918 | C & B Graham Energy | AlertRecipients | Pass | Pass |  | 100
S65918 | C & B Graham Energy | CheckHW | Fail | Fail | Fail: 0.00 % Tracker Control 3 (1-86): Suggested tracker configuration, Initial angle: , GCR: , GCR West: Tracker Control 3 (87-103): Alerts not set on Tracker Control 3 (87-103): Suggested tracker configuration, Initial angle: , GCR: , GCR West: | 0 | {'index': 0, 'result': 3, 'detail': 'Suggested tracker configuration, Initial angle: , GCR: , GCR West: ', 'success': 0.0, 'hardwareKey': 'H494074', 'hardwareName': 'Tracker Control 3 (1-86)', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Alerts not set on ', 'success': 0.0, 'hardwareKey': 'H494075', 'hardwareName': 'Tracker Control 3 (87-103)', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Suggested tracker configuration, Initial angle: , GCR: , GCR West: ', 'success': 0.0, 'hardwareKey': 'H494075', 'hardwareName': 'Tracker Control 3 (87-103)', 'isAcknowledged': False}
S65918 | C & B Graham Energy | CheckSysSize | Pass | Pass |  | 100
S65918 | C & B Graham Energy | DefaultAlerts | Fail | Fail | Fail: 0.00 % TRACKER CONTROL 1: Default alerts not set: 974 TRACKER CONTROL 2: Default alerts not set: 974 Tracker Control 3 (1-86): Default alerts not set: 2535 Tracker Control 3 (87-103): Default alerts not set: 250,2535 ALSOENERGY SMART UPS: Default alerts not set: 250,3618 | 0 | {'index': 0, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 974\t', 'success': 0.0, 'hardwareKey': 'H449763', 'hardwareName': 'TRACKER CONTROL 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 974\t', 'success': 0.0, 'hardwareKey': 'H449764', 'hardwareName': 'TRACKER CONTROL 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Default alerts not set: \t\t\t 2535\t', 'success': 0.0, 'hardwareKey': 'H494074', 'hardwareName': 'Tracker Control 3 (1-86)', 'isAcknowledged': False}
S65918 | C & B Graham Energy | HasPVmodel | Pass | Pass |  | 100
S65918 | C & B Graham Energy | HasWSmodel | Pass | Pass |  | 100
S65918 | C & B Graham Energy | InvalidAlerts | Fail | Fail | Fail: 0.00 % INVERTER 1: Alerts not valid: 1037 INVERTER 2: Alerts not valid: 1037 INVERTER 3: Alerts not valid: 1037 INVERTER 4: Alerts not valid: 1037 INVERTER 5: Alerts not valid: 1037 INVERTER 6: Alerts not valid: 1037 INVERTER 7: Alerts not valid: 1037 INVERTER 8: Alerts not valid: 1037 INVERTER 9: Alerts not valid: 1037 INVERTER 10: Alerts not valid: 1037 INVERTER 11: Alerts not valid: 1037 INVERTER 12: Alerts not valid: 1037 INVERTER 13: Alerts not valid: 1037 INVERTER 14: Alerts not valid: 1037 INVERTER 15: Alerts not valid: 1037 INVERTER 16: Alerts not valid: 1037 INVERTER 17: Alerts not valid: 1037 INVERTER 18: Alerts not valid: 1037 INVERTER 19: Alerts not valid: 1037 INVERTER 20: Alerts not valid: 1037 INVERTER 21: Alerts not valid: 1037 INVERTER 22: Alerts not valid: 1037 INVERTER 23: Alerts not valid: 1037 INVERTER 24: Alerts not valid: 1037 INVERTER 25: Alerts not valid: 1037 INVERTER 26: Alerts not valid: 1037 INVERTER 27: Alerts not valid: 1037 INVERTER 28: Alerts not valid: 1037 INVERTER 29: Alerts not valid: 1037 INVERTER 30: Alerts not valid: 1037 INVERTER 31: Alerts not valid: 1037 INVERTER 32: Alerts not valid: 1037 INVERTER 33: Alerts not valid: 1037 INVERTER 34: Alerts not valid: 1037 INVERTER 35: Alerts not valid: 1037 Tracker Control 3 (1-86): Alerts not valid: 593 INVERTER 1: Alert ' Solectria XGI 1500 Series - Fault Alert ' triggered 12 times in the past 24 hours. INVERTER 4: Alert ' Solectria XGI 1500 Series - Fault Alert ' triggered 40 times in the past 24 hours. | 0 | {'index': 0, 'result': 3, 'detail': 'Alerts not valid: \t\t\t 1037\t', 'success': 0.0, 'hardwareKey': 'H449723', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Alerts not valid: \t\t\t 1037\t', 'success': 0.0, 'hardwareKey': 'H449724', 'hardwareName': 'INVERTER 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Alerts not valid: \t\t\t 1037\t', 'success': 0.0, 'hardwareKey': 'H449725', 'hardwareName': 'INVERTER 3', 'isAcknowledged': False}
S65918 | C & B Graham Energy | SiteConfig | Pass | Pass |  | 100
S65918 | C & B Graham Energy | CheckWeather | Fail | Fail | Fail: 0.00 % WEATHER STATION: Invalid ambient temperature WEATHER STATION: Invalid module temperature PYRANOMETER - POA: Invalid irradiance: PYRANOMETER - GHI: Invalid irradiance: PYRANOMETER - BPOA: Invalid irradiance: | 0 | {'index': 0, 'result': 3, 'detail': 'Invalid ambient temperature', 'success': 0.0, 'hardwareKey': 'H449758', 'hardwareName': 'WEATHER STATION', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Invalid module temperature ', 'success': 0.0, 'hardwareKey': 'H449758', 'hardwareName': 'WEATHER STATION', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Invalid irradiance: ', 'success': 0.0, 'hardwareKey': 'H449759', 'hardwareName': 'PYRANOMETER - POA', 'isAcknowledged': False}
S65918 | C & B Graham Energy | DataCuration | Pass | Pass |  | 100
S65918 | C & B Graham Energy | kWandkWh | Pass | Pass |  | 100
S65918 | C & B Graham Energy | PVPMenergy | Fail | Fail | Fail: 0.00 % METER - PRODUCTION 1: Energy data not found METER - PRODUCTION 2: Inverter / meter energy correlation: % METER - PRODUCTION 3: Inverter / meter energy correlation: % | 0 | {'index': 0, 'result': 3, 'detail': 'Energy data not found', 'success': 0.0, 'hardwareKey': 'H449718', 'hardwareName': 'METER - PRODUCTION 1', 'isAcknowledged': False}
S65918 | C & B Graham Energy | Tracker | Fail | Fail | Fail: 0.00 % TRACKER CONTROL 1: Tracker ' Position A1 S 29 ' always -181.869 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 10 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 16 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 26 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 37 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 43 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 85 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 88 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 94 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 96 ' always 0 degrees TRACKER CONTROL 2: Tracker ' Position A1 S 98 ' always 0 degrees Tracker Control 3 (1-86): Tracker ' Angular Position_32 ' always 0 degrees Tracker Control 3 (1-86): Tracker ' Angular Position_42 ' always 0 degrees Tracker Control 3 (87-103): Tracker ' Angular Position_96 ' always 0 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 1 ): 36.60443 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 2 ): 35.398069 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 3 ): 35.473205 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 4 ): 37.3064 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 5 ): 37.386015 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 6 ): 35.36375 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 7 ): 37.03705 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 8 ): 36.664649999999995 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 9 ): 37.025425 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 10 ): 36.17552 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 11 ): 36.568464999999996 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 12 ): 36.62275 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 13 ): 37.23374 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 14 ): 36.84333 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 15 ): 37.845535 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 16 ): 37.122265 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 17 ): 37.10747 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 18 ): 37.52627 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 19 ): 37.114545 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 20 ): 37.214749999999995 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 21 ): 36.716745 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 22 ): 37.20455 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 23 ): 36.315255 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 24 ): 36.483045000000004 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 25 ): 37.11596 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 26 ): 36.700495000000004 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 27 ): 36.912385 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 28 ): 36.91099 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 30 ): 36.71189 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 31 ): 37.69821 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 32 ): 36.91984 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 33 ): 37.25204 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 34 ): 37.130945 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 35 ): 36.800875 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 36 ): 36.66789 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 37 ): 36.734805 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 38 ): 36.86004 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 39 ): 36.710544999999996 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 40 ): 36.792145 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 41 ): 36.800195 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 42 ): 36.766040000000004 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 43 ): 36.998355 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 44 ): 36.92248 degrees TRACKER CONTROL 1: Average tracker error ( Position A1 S 45 ): 37.03638 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 9 ): 40.48992 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 36 ): 39.657579999999996 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 45 ): 39.45819 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 46 ): 39.64009 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 47 ): 39.63535 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 48 ): 39.684235 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 50 ): 39.63808 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 52 ): 39.68015 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 62 ): 39.66643 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 63 ): 39.58095 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 79 ): 39.621065 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 83 ): 39.513400000000004 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 84 ): 39.615449999999996 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 86 ): 39.667024999999995 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 89 ): 39.60059 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 90 ): 39.65487 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 91 ): 39.541985 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 92 ): 39.5851 degrees TRACKER CONTROL 2: Average tracker error ( Position A1 S 93 ): 39.665800000000004 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_1 ): 34.363115 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_2 ): 33.796235 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_3 ): 34.018755 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_4 ): 33.347135 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_5 ): 33.990625 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_6 ): 34.182230000000004 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_7 ): 33.760075 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_8 ): 33.50641 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_9 ): 33.702495 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_10 ): 33.73391 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_11 ): 32.9995 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_12 ): 33.23004 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_13 ): 33.88996 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_14 ): 33.67888 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_15 ): 34.000175 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_16 ): 33.686945 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_17 ): 33.76337 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_18 ): 33.489695 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_19 ): 34.066914999999995 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_20 ): 33.20401 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_21 ): 33.510639999999995 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_22 ): 33.012945 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_23 ): 33.40493 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_24 ): 33.224235 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_25 ): 33.127365 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_26 ): 33.531355 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_27 ): 33.37929 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_28 ): 32.458895 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_29 ): 33.43704 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_30 ): 33.418605 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_31 ): 33.83418 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_33 ): 33.993134999999995 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_34 ): 33.427355 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_35 ): 33.36999 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_36 ): 33.46027 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_37 ): 33.47694 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_38 ): 32.621525 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_39 ): 33.01531 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_40 ): 32.89142 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_41 ): 33.78575 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_43 ): 33.143765 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_44 ): 33.280235 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_45 ): 52.217945 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_46 ): 34.120365 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_47 ): 33.645995 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_48 ): 35.576965 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_49 ): 34.582795000000004 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_50 ): 36.12955 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_51 ): 34.36486 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_52 ): 33.735254999999995 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_53 ): 34.04947 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_54 ): 33.7372 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_55 ): 34.33161 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_56 ): 33.837415 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_57 ): 34.088699999999996 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_58 ): 33.423305 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_59 ): 33.850269999999995 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_60 ): 34.24359 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_61 ): 34.17618 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_62 ): 34.319345 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_63 ): 33.828165 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_64 ): 34.24288 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_65 ): 34.25721 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_66 ): 34.438655 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_67 ): 34.09981 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_68 ): 34.31692 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_69 ): 34.072565 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_70 ): 34.111850000000004 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_71 ): 33.66964 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_72 ): 33.43755 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_73 ): 33.890209999999996 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_74 ): 34.346975 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_75 ): 33.710840000000005 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_76 ): 33.79709 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_77 ): 33.716300000000004 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_78 ): 33.36179 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_79 ): 33.641315 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_80 ): 33.811335 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_81 ): 33.686835 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_82 ): 28.207315 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_83 ): 33.789075 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_84 ): 33.4059 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_85 ): 33.625429999999994 degrees Tracker Control 3 (1-86): Average tracker error ( Angular Position_86 ): 33.73556 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_87 ): 34.00876 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_88 ): 33.458225 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_89 ): 33.524505 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_90 ): 33.293504999999996 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_91 ): 33.83748 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_92 ): 33.656225 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_93 ): 33.604835 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_94 ): 33.243905 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_95 ): 52.233325 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_97 ): 33.6139 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_98 ): 33.709955 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_99 ): 33.29824 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_100 ): 34.18173 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_101 ): 34.23937 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_102 ): 32.6341 degrees Tracker Control 3 (87-103): Average tracker error ( Angular Position_103 ): 33.156545 degrees | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 29\t' always \t\t\t -181.869\t degrees", 'success': 0.0, 'hardwareKey': 'H449763', 'hardwareName': 'TRACKER CONTROL 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 10\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H449764', 'hardwareName': 'TRACKER CONTROL 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': "Tracker '\t\t\t Position A1 S 16\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H449764', 'hardwareName': 'TRACKER CONTROL 2', 'isAcknowledged': False}
S65918 | C & B Graham Energy | EnergyRatio | Fail | Fail | Fail: 0.00 % METER - PRODUCTION 1: Unable to calculate energy ratio METER - PRODUCTION 2: Unable to calculate energy ratio METER - PRODUCTION 3: Unable to calculate energy ratio | 0 | {'index': 0, 'result': 3, 'detail': 'Unable to calculate energy ratio', 'success': 0.0, 'hardwareKey': 'H449718', 'hardwareName': 'METER - PRODUCTION 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Unable to calculate energy ratio', 'success': 0.0, 'hardwareKey': 'H449720', 'hardwareName': 'METER - PRODUCTION 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Unable to calculate energy ratio', 'success': 0.0, 'hardwareKey': 'H449722', 'hardwareName': 'METER - PRODUCTION 3', 'isAcknowledged': False}
S65918 | C & B Graham Energy | ProductionEnergy | Pass | Pass |  | 100
S65918 | C & B Graham Energy | PVlosses | Fail | Fail | Fail: 0.00 % INVERTER 1: Unable to calculate PV losses INVERTER 2: Unable to calculate PV losses INVERTER 3: Unable to calculate PV losses INVERTER 4: Unable to calculate PV losses INVERTER 5: Unable to calculate PV losses INVERTER 6: Unable to calculate PV losses INVERTER 7: Unable to calculate PV losses INVERTER 8: Unable to calculate PV losses INVERTER 9: Unable to calculate PV losses INVERTER 10: Unable to calculate PV losses INVERTER 11: Unable to calculate PV losses INVERTER 12: Unable to calculate PV losses INVERTER 13: Unable to calculate PV losses INVERTER 14: Unable to calculate PV losses INVERTER 15: Unable to calculate PV losses INVERTER 16: Unable to calculate PV losses INVERTER 17: Unable to calculate PV losses INVERTER 18: Unable to calculate PV losses INVERTER 19: Unable to calculate PV losses INVERTER 20: Unable to calculate PV losses INVERTER 21: Unable to calculate PV losses INVERTER 22: Unable to calculate PV losses INVERTER 23: Unable to calculate PV losses INVERTER 24: Unable to calculate PV losses INVERTER 25: Unable to calculate PV losses INVERTER 26: Unable to calculate PV losses INVERTER 27: Unable to calculate PV losses INVERTER 28: Unable to calculate PV losses INVERTER 29: Unable to calculate PV losses INVERTER 30: Unable to calculate PV losses INVERTER 31: Unable to calculate PV losses INVERTER 32: Unable to calculate PV losses INVERTER 33: Unable to calculate PV losses INVERTER 34: Unable to calculate PV losses INVERTER 35: Unable to calculate PV losses | 0 | {'index': 0, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H449723', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H449724', 'hardwareName': 'INVERTER 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Unable to calculate PV losses', 'success': 0.0, 'hardwareKey': 'H449725', 'hardwareName': 'INVERTER 3', 'isAcknowledged': False}
S65918 | C & B Graham Energy | PVmodelEnergy24 | Fail | Fail | Energy above expected ( ∞ %) | NaN | {'index': 0, 'result': 3, 'detail': 'Energy above expected (\t\t\t ∞\t %)', 'success': 'Infinity', 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S65918 | C & B Graham Energy | CorrectiveAction | Fail | Fail | Fail: 0.00 % Equipment repair required due to production capacity loss of 146 % ( 10189 kW). ( Low availability ), Production meter : METER - PRODUCTION 1 Equipment repair required. Low availability , Weather station : WEATHER STATION, PYRANOMETER - POA, PYRANOMETER - GHI, PYRANOMETER - BPOA | 0 | {'index': 0, 'result': 3, 'detail': 'Equipment repair required due to production capacity loss of \t\t\t 146\t % (\t\t\t 10189\t kW). (\t\t\t Low availability\t), \t\t\t Production meter\t: \t\t\t METER - PRODUCTION 1\t', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Low availability\t, \t\t\t Weather station\t: \t\t\t WEATHER STATION, PYRANOMETER - POA, PYRANOMETER - GHI, PYRANOMETER - BPOA\t', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S66000 | Auburn Solar | Availability | Pass | Pass |  | 100
S66000 | Auburn Solar | CheckUpload | Pass | Pass |  | 100
S66000 | Auburn Solar | InverterUptime | Pass | Pass |  | 100
S66000 | Auburn Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 9 of 9 TCP devices communicating normally DATALOGGER: 3 of 3 devices on port 2 communicating normally DATALOGGER: 1 of 1 devices on port 1 communicating normally | 100
S66000 | Auburn Solar | AlertRecipients | Pass | Pass |  | 100
S66000 | Auburn Solar | CheckHW | Pass | Pass |  | 100
S66000 | Auburn Solar | CheckSysSize | Pass | Pass |  | 100
S66000 | Auburn Solar | DefaultAlerts | Pass | Pass |  | 100
S66000 | Auburn Solar | HasPVmodel | Pass | Pass |  | 100
S66000 | Auburn Solar | HasWSmodel | Pass | Pass |  | 100
S66000 | Auburn Solar | InvalidAlerts | Pass | Pass |  | 100
S66000 | Auburn Solar | SiteConfig | Pass | Pass |  | 100
S66000 | Auburn Solar | CheckMeterVoltage | Pass | Pass |  | 100
S66000 | Auburn Solar | CheckWeather | Fail | Fail | PYRANOMETER - POA: The POA sensor, "", appears to be fixed tilt and is configured for a tracker. | 0 | {'index': 0, 'result': 3, 'detail': 'The POA sensor, "", appears to be fixed tilt and is configured for a tracker.', 'success': 0.0, 'hardwareKey': 'H463766', 'hardwareName': 'PYRANOMETER - POA', 'isAcknowledged': False}
S66000 | Auburn Solar | DataCuration | Pass | Pass |  | 100
S66000 | Auburn Solar | kWandkWh | Pass | Pass |  | 100
S66000 | Auburn Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 98.7254
S66000 | Auburn Solar | Tracker | Pass | Pass |  | 100
S66000 | Auburn Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.75061695573524 %, PF: 0.9665639647290335 | 99.7506
S66000 | Auburn Solar | ProductionEnergy | Pass | Pass |  | 100
S66000 | Auburn Solar | PVlosses | Pass | Pass |  | 100
S66000 | Auburn Solar | PVmodelEnergy24 | Pass | Pass |  | 108.4383
S66000 | Auburn Solar | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S66001 | Sheridan Solar | Availability | Pass | Pass |  | 100
S66001 | Sheridan Solar | CheckUpload | Pass | Pass |  | 100
S66001 | Sheridan Solar | InverterUptime | Pass | Pass |  | 100
S66001 | Sheridan Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 9 of 9 TCP devices communicating normally DATALOGGER: 3 of 3 devices on port 2 communicating normally DATALOGGER: 1 of 1 devices on port 1 communicating normally | 100
S66001 | Sheridan Solar | AlertRecipients | Pass | Pass |  | 100
S66001 | Sheridan Solar | CheckHW | Pass | Pass |  | 100
S66001 | Sheridan Solar | CheckSysSize | Pass | Pass |  | 100
S66001 | Sheridan Solar | DefaultAlerts | Pass | Pass |  | 100
S66001 | Sheridan Solar | HasPVmodel | Pass | Pass |  | 100
S66001 | Sheridan Solar | HasWSmodel | Pass | Pass |  | 100
S66001 | Sheridan Solar | InvalidAlerts | Pass | Pass |  | 100
S66001 | Sheridan Solar | SiteConfig | Pass | Pass |  | 100
S66001 | Sheridan Solar | CheckMeterVoltage | Pass | Pass |  | 100
S66001 | Sheridan Solar | CheckWeather | Fail | Fail | WEATHER STATION: Temperature too high: | 0 | {'index': 0, 'result': 3, 'detail': 'Temperature too high: ', 'success': 0.0, 'hardwareKey': 'H460778', 'hardwareName': 'WEATHER STATION', 'isAcknowledged': False}
S66001 | Sheridan Solar | DataCuration | Pass | Pass |  | 100
S66001 | Sheridan Solar | kWandkWh | Pass | Pass |  | 100
S66001 | Sheridan Solar | PVPMenergy | Pass | Pass | METER - NET: Inverter / meter energy correlation: % | 98.2995
S66001 | Sheridan Solar | Tracker | Pass | Pass |  | 100
S66001 | Sheridan Solar | CheckPMCTs | Pass | Pass | METER - NET: Phase current ratio 98.52894681546738 %, PF: 1 | 98.5289
S66001 | Sheridan Solar | EnergyRatio | Pass | Pass |  | 94.7885
S66001 | Sheridan Solar | ProductionEnergy | Pass | Pass |  | 100
S66001 | Sheridan Solar | PVlosses | Pass | Pass |  | 100
S66001 | Sheridan Solar | PVmodelEnergy24 | Pass | Pass |  | 96.2646
S66001 | Sheridan Solar | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S66930 | Elk Solar | Availability | Fail | Fail | Fail: 0.00 % SEL 735 Production Meter: Availability: 0 % 11 String: Availability: 0 % 10 String: Availability: 0 % Inverter - 02.01: Availability: 97.95918367346938 % Inverter - 02.02: Availability: 97.95918367346938 % Inverter - 02.03: Availability: 97.95918367346938 % Inverter - 02.05: Availability: 97.95918367346938 % Inverter - 01.02: Availability: 0 % Inverter - 01.03: Availability: 97.95918367346938 % Inverter - 01.04: Availability: 97.95918367346938 % Inverter - 01.06: Availability: 97.95918367346938 % Inverter - 03.01: Availability: 97.95918367346938 % Inverter - 03.02: Availability: 97.95918367346938 % Inverter - 03.04: Availability: 97.95918367346938 % Inverter - 03.05: Availability: 97.95918367346938 % Inverter - 01.07: Availability: 97.95918367346938 % Inverter - 01.08: Availability: 97.95918367346938 % Inverter - 01.14: Availability: 91.83673469387755 % Inverter - 02.08: Availability: 97.95918367346938 % Inverter - 02.13: Availability: 97.95918367346938 % Inverter - 03.07: Availability: 97.95918367346938 % Inverter - 03.08: Availability: 97.95918367346938 % Inverter - 03.09: Availability: 97.95918367346938 % Inverter - 03.10: Availability: 97.95918367346938 % Inverter - 03.11: Availability: 97.95918367346938 % Inverter - 03.12: Availability: 97.95918367346938 % Inverter - 03.13: Availability: 97.95918367346938 % Inverter - 03.14: Availability: 97.95918367346938 % Inverter - 01.15: Availability: 95.91836734693878 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H498894', 'hardwareName': 'SEL 735 Production Meter', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H595414', 'hardwareName': '11 String', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H595415', 'hardwareName': '10 String', 'isAcknowledged': False}
S66930 | Elk Solar | CheckUpload | Fail | Fail | Inverter - 01.02: Last upload: 5/27/2026 3:25 AM ( US/Eastern ), delay: 12 d 1.4 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 5/27/2026 3:25 AM\t (\t\t\t US/Eastern\t), delay: \t\t\t 12 d 1.4 h\t', 'success': 0.0, 'hardwareKey': 'H499741', 'hardwareName': 'Inverter - 01.02', 'isAcknowledged': False}
S66930 | Elk Solar | InverterUptime | Fail | Fail | Fail: 0.00 % 11 String: Inverter uptime: 95.523370638578 % 10 String: Inverter uptime: 98.2993197278912 % 2 of 43 inverters failed to achieve an uptime of 100 % | 0 | {'index': 0, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 95.523370638578\t %', 'success': 0.0, 'hardwareKey': 'H595414', 'hardwareName': '11 String', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 98.2993197278912\t %', 'success': 0.0, 'hardwareKey': 'H595415', 'hardwareName': '10 String', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': '\t\t\t 2\t of \t\t\t 43\t inverters failed to achieve an uptime of \t\t\t 100\t %', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S66930 | Elk Solar | AlertRecipients | Pass | Pass |  | 100
S66930 | Elk Solar | CheckHW | Fail | Fail | Fail: 0.00 % 11 String: Inverter group devices that don't receive data should be set to 'Offline'. 10 String: Inverter group devices that don't receive data should be set to 'Offline'. | 0 | {'index': 0, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H595414', 'hardwareName': '11 String', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H595415', 'hardwareName': '10 String', 'isAcknowledged': False}
S66930 | Elk Solar | CheckSysSize | Pass | Pass |  | 100
S66930 | Elk Solar | DefaultAlerts | Pass | Pass |  | 100
S66930 | Elk Solar | HasPVmodel | Pass | Pass |  | 100
S66930 | Elk Solar | HasWSmodel | Pass | Pass |  | 100
S66930 | Elk Solar | InvalidAlerts | Pass | Pass |  | 100
S66930 | Elk Solar | SiteConfig | Pass | Pass |  | 100
S66930 | Elk Solar | CheckMeterVoltage | Fail | Fail | SEL 735 Production Meter: Calculated power from phase voltage and current is 173.11653463278668 % of meter power | 0 | {'index': 0, 'result': 3, 'detail': 'Calculated power from phase voltage and current is \t\t\t 173.11653463278668\t % of meter power', 'success': 0.0, 'hardwareKey': 'H498894', 'hardwareName': 'SEL 735 Production Meter', 'isAcknowledged': False}
S66930 | Elk Solar | CheckWeather | Fail | Fail | Weather Station: Insolation mismatch + 25.49448628384572 % (higher than other sensors), check azimuth/tilt settings: Plane of Array Irradiance | 0 | {'index': 0, 'result': 3, 'detail': 'Insolation mismatch +\t\t\t 25.49448628384572\t % (higher than other sensors), check azimuth/tilt settings: \t\t\t Plane of Array Irradiance\t', 'success': 0.0, 'hardwareKey': 'H498892', 'hardwareName': 'Weather Station', 'isAcknowledged': False}
S66930 | Elk Solar | DataCuration | Pass | Pass |  | 100
S66930 | Elk Solar | kWandkWh | Pass | Pass |  | 100
S66930 | Elk Solar | PVPMenergy | Fail | Fail | SEL 735 Production Meter: Energy data not found | 0 | {'index': 0, 'result': 3, 'detail': 'Energy data not found', 'success': 0.0, 'hardwareKey': 'H498894', 'hardwareName': 'SEL 735 Production Meter', 'isAcknowledged': False}
S66930 | Elk Solar | Tracker | Fail | Fail | Fail: 0.00 % NCU 2: Tracker ' Tracker Position 255 ' always 0 degrees NCU 1: Average tracker error ( Tracker Position 126 ): 65.81432 degrees NCU 2: Average tracker error ( Tracker Position 257 ): 10.14079 degrees NCU 2: Average tracker error ( Tracker Position 260 ): 32.28752 degrees NCU 2: Average tracker error ( Tracker Position 268 ): 31.39285 degrees NCU 2: Average tracker error ( Tracker Position 270 ): 5.040447 degrees NCU 1: High tracker motor current ( Motor Current 121 ), ( 41.55463191489362 amps, 165.44158431939246 % of average) NCU 1: Low tracker motor current ( Motor Current 126 ), ( 0 amps, 0 % of average) NCU 1: High tracker motor current ( Motor Current 155 ), ( 42.25531489361702 amps, 168.25882621902963 % of average) NCU 1: High tracker motor current ( Motor Current 161 ), ( 38.76311893617021 amps, 154.22689825419747 % of average) NCU 1: High tracker motor current ( Motor Current 164 ), ( 43.51916957446808 amps, 173.34275631344235 % of average) NCU 1: High tracker motor current ( Motor Current 183 ), ( 38.26237382978724 amps, 152.21674365929118 % of average) NCU 2: High tracker motor current ( Motor Current 205 ), ( 38.45463404255319 amps, 152.98848330199417 % of average) NCU 2: High tracker motor current ( Motor Current 212 ), ( 85.12623191489362 amps, 342.4073297369739 % of average) NCU 2: High tracker motor current ( Motor Current 224 ), ( 39.795731914893615 amps, 158.3736323637441 % of average) NCU 2: High tracker motor current ( Motor Current 232 ), ( 42.44255531914893 amps, 169.01182194335655 % of average) NCU 2: High tracker motor current ( Motor Current 239 ), ( 43.13616659574468 amps, 171.8017862725785 % of average) NCU 2: Low tracker motor current ( Motor Current 255 ), ( 0 amps, 0 % of average) NCU 2: High tracker motor current ( Motor Current 259 ), ( 121.74043617021277 amps, 493.96171004912594 % of average) NCU 2: Low tracker motor current ( Motor Current 260 ), ( 0 amps, 0 % of average) NCU 2: High tracker motor current ( Motor Current 262 ), ( 88.25245744680852 amps, 355.24486864245586 % of average) NCU 2: High tracker motor current ( Motor Current 264 ), ( 61.35034042553191 amps, 245.39194711446297 % of average) NCU 2: High tracker motor current ( Motor Current 267 ), ( 54.48792978723405 amps, 217.59202856604998 % of average) NCU 2: Low tracker motor current ( Motor Current 268 ), ( 0 amps, 0 % of average) | 0 | {'index': 0, 'result': 3, 'detail': "Tracker '\t\t\t Tracker Position 255\t' always \t\t\t 0\t degrees", 'success': 0.0, 'hardwareKey': 'H498891', 'hardwareName': 'NCU 2', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Average tracker error (\t\t\t Tracker Position 126\t): \t\t\t 65.81432\t degrees', 'success': 0.0, 'hardwareKey': 'H498890', 'hardwareName': 'NCU 1', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Average tracker error (\t\t\t Tracker Position 257\t): \t\t\t 10.14079\t degrees', 'success': 0.0, 'hardwareKey': 'H498891', 'hardwareName': 'NCU 2', 'isAcknowledged': False}
S66930 | Elk Solar | CheckPMCTs | Pass | Pass | SEL 735 Production Meter: Phase current ratio 99.92633537593512 %, PF: 0.9951111152095778 | 99.9263
S66930 | Elk Solar | EnergyRatio | Fail | Fail | Fail: 0.00 % Inverter - 01.01: Low energy ratio: 0.34832308189272926 Inverter - 01.05: Low energy ratio: 0.4996174281271735 SEL 735 Production Meter: Unable to calculate energy ratio | 0 | {'index': 0, 'result': 3, 'detail': 'Low energy ratio: \t\t\t 0.34832308189272926\t', 'success': 0.0, 'hardwareKey': 'H499740', 'hardwareName': 'Inverter - 01.01', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Low energy ratio: \t\t\t 0.4996174281271735\t', 'success': 0.0, 'hardwareKey': 'H499744', 'hardwareName': 'Inverter - 01.05', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Unable to calculate energy ratio', 'success': 0.0, 'hardwareKey': 'H498894', 'hardwareName': 'SEL 735 Production Meter', 'isAcknowledged': False}
S66930 | Elk Solar | ProductionEnergy | Pass | Pass |  | 100
S66930 | Elk Solar | PVlosses | Fail | Fail | Fail: 0.00 % Inverter - 02.04: Excessive soiling loss: 5.90783522338646 % ( 69.8784607634 kWh) Inverter - 02.06: Excessive soiling loss: 6.623578164982029 % ( 78.34433923999995 kWh) Inverter - 01.01: Excessive residual loss: 64.60933692343397 % Inverter - 01.02: Downtime loss detected: 99.9297666818894 % ( 1181.9791879999998 kWh) Inverter - 01.05: Excessive residual loss: 48.9897990167986 % Inverter - 02.10: Excessive soiling loss: 6.811471604001576 % ( 80.5667614657 kWh) | 0 | {'index': 0, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 5.90783522338646\t % (\t\t\t 69.8784607634\t kWh)', 'success': 0.0, 'hardwareKey': 'H499737', 'hardwareName': 'Inverter - 02.04', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Excessive soiling loss: \t\t\t 6.623578164982029\t % (\t\t\t 78.34433923999995\t kWh)', 'success': 0.0, 'hardwareKey': 'H499739', 'hardwareName': 'Inverter - 02.06', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Excessive residual loss: \t\t\t 64.60933692343397\t %', 'success': 0.0, 'hardwareKey': 'H499740', 'hardwareName': 'Inverter - 01.01', 'isAcknowledged': False}
S66930 | Elk Solar | PVmodelEnergy24 | Fail | Fail | Energy below expected ( 0 %) | 0 | {'index': 0, 'result': 3, 'detail': 'Energy below expected (\t\t\t 0\t %)', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S66930 | Elk Solar | CorrectiveAction | Fail | Fail | Fail: 0.00 % Corrective action recommended, ( kWh/day loss). Equipment repair required due to production capacity loss of 100 % ( 5375 kW). ( Low availability ), Production meter, PV system inverter : SEL 735 Production Meter, Inverter - 02.01, Inverter - 02.02, Inverter - 02.03, Inverter - 02.05, Inverter - 01.02, Inverter - 01.03, Inverter - 01.04, Inverter - 01.06, Inverter - 03.01, Inverter - 03.02, Inverter - 03.04, Inverter - 03.05, Inverter - 01.07, Inverter - 01.08, Inverter - 01.14, Inverter - 02.08, Inverter - 02.13, Inverter - 03.07, Inverter - 03.08, Inverter - 03.09, Inverter - 03.10, Inverter - 03.11, Inverter - 03.12, Inverter - 03.13, Inverter - 03.14, Inverter - 01.15 Equipment repair required. Low availability , Inverter group : 11 String, 10 String | 0 | {'index': 0, 'result': 3, 'detail': 'Corrective action recommended, ( kWh/day loss). ', 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Equipment repair required due to production capacity loss of \t\t\t 100\t % (\t\t\t 5375\t kW). (\t\t\t Low availability\t), \t\t\t Production meter, PV system inverter\t: \t\t\t SEL 735 Production Meter, Inverter - 02.01, Inverter - 02.02, Inverter - 02.03, Inverter - 02.05, Inverter - 01.02, Inverter - 01.03, Inverter - 01.04, Inverter - 01.06, Inverter - 03.01, Inverter - 03.02, Inverter - 03.04, Inverter - 03.05, Inverter - 01.07, Inverter - 01.08, Inverter - 01.14, Inverter - 02.08, Inverter - 02.13, Inverter - 03.07, Inverter - 03.08, Inverter - 03.09, Inverter - 03.10, Inverter - 03.11, Inverter - 03.12, Inverter - 03.13, Inverter - 03.14, Inverter - 01.15\t', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Equipment repair required. \t\t\t Low availability\t, \t\t\t Inverter group\t: \t\t\t 11 String, 10 String\t', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S68112 | Wallace Solar | Availability | Pass | Pass |  | 100
S68112 | Wallace Solar | CheckUpload | Pass | Pass |  | 100
S68112 | Wallace Solar | InverterUptime | Pass | Pass |  | 100
S68112 | Wallace Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 7 of 7 TCP devices communicating normally DATALOGGER: 2 of 2 devices on port 2 communicating normally DATALOGGER: 2 of 2 devices on port 1 communicating normally | 100
S68112 | Wallace Solar | AlertRecipients | Pass | Pass |  | 100
S68112 | Wallace Solar | CheckHW | Pass | Pass |  | 100
S68112 | Wallace Solar | CheckSysSize | Pass | Pass |  | 100
S68112 | Wallace Solar | DefaultAlerts | Pass | Pass |  | 100
S68112 | Wallace Solar | HasPVmodel | Pass | Pass |  | 100
S68112 | Wallace Solar | HasWSmodel | Pass | Pass |  | 100
S68112 | Wallace Solar | InvalidAlerts | Pass | Pass |  | 100
S68112 | Wallace Solar | SiteConfig | Pass | Pass |  | 100
S68112 | Wallace Solar | CheckMeterVoltage | Pass | Pass |  | 100
S68112 | Wallace Solar | CheckWeather | Fail | Fail | Fail: 0.00 % PYRANOMETER - BPOA: Insolation low, : < PYRANOMETER - GHI: Insolation mismatch 105.79132070161116 %, check azimuth/tilt settings: Sun (GHI Temp comp) (this is a secondary sensor) PYRANOMETER - POA: Insolation mismatch + 54.53426997384691 % (higher than other sensors), check azimuth/tilt settings: Sun (POA Temp comp) PYRANOMETER - BPOA: Insolation mismatch -87.91440324656627 %, check azimuth/tilt settings: Sun (POA Temp comp) (this is a secondary sensor) | 0 | {'index': 0, 'result': 3, 'detail': 'Insolation low, : < ', 'success': 0.0, 'hardwareKey': 'H499000', 'hardwareName': 'PYRANOMETER - BPOA', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Insolation mismatch +\t\t\t 54.53426997384691\t % (higher than other sensors), check azimuth/tilt settings: \t\t\t Sun (POA Temp comp)\t', 'success': 0.0, 'hardwareKey': 'H498999', 'hardwareName': 'PYRANOMETER - POA', 'isAcknowledged': False}
S68112 | Wallace Solar | DataCuration | Pass | Pass |  | 100
S68112 | Wallace Solar | kWandkWh | Pass | Pass |  | 100
S68112 | Wallace Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 98.5867
S68112 | Wallace Solar | Tracker | Pass | Pass |  | 100
S68112 | Wallace Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 98.53394132829085 %, PF: 0.9970569311036335 | 98.5339
S68112 | Wallace Solar | EnergyRatio | Fail | Fail | Fail: 0.00 % INVERTER 1: High energy ratio: 1.14183802218868 METER - PRODUCTION: High energy ratio: 1.1260026036098145 | 0 | {'index': 0, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.14183802218868\t', 'success': 0.0, 'hardwareKey': 'H498997', 'hardwareName': 'INVERTER 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'High energy ratio: \t\t\t 1.1260026036098145\t', 'success': 0.0, 'hardwareKey': 'H498995', 'hardwareName': 'METER - PRODUCTION', 'isAcknowledged': False}
S68112 | Wallace Solar | ProductionEnergy | Pass | Pass |  | 100
S68112 | Wallace Solar | PVlosses | Pass | Pass |  | 100
S68112 | Wallace Solar | PVmodelEnergy24 | Pass | Pass |  | 112.5914
S68112 | Wallace Solar | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S68113 | Marble Solar | Availability | Pass | Pass |  | 100
S68113 | Marble Solar | CheckUpload | Pass | Pass |  | 100
S68113 | Marble Solar | InverterUptime | Pass | Pass |  | 100
S68113 | Marble Solar | NetworkCom | Pass | Pass | Pass: 100.00 % DATALOGGER: 7 of 7 TCP devices communicating normally DATALOGGER: 2 of 2 devices on port 2 communicating normally DATALOGGER: 2 of 2 devices on port 1 communicating normally | 100
S68113 | Marble Solar | AlertRecipients | Pass | Pass |  | 100
S68113 | Marble Solar | CheckHW | Pass | Pass |  | 100
S68113 | Marble Solar | CheckSysSize | Pass | Pass |  | 100
S68113 | Marble Solar | DefaultAlerts | Pass | Pass |  | 100
S68113 | Marble Solar | HasPVmodel | Pass | Pass |  | 100
S68113 | Marble Solar | HasWSmodel | Pass | Pass |  | 100
S68113 | Marble Solar | InvalidAlerts | Pass | Pass |  | 100
S68113 | Marble Solar | SiteConfig | Pass | Pass |  | 100
S68113 | Marble Solar | CheckMeterVoltage | Pass | Pass |  | 100
S68113 | Marble Solar | CheckWeather | Pass | Pass |  | 100
S68113 | Marble Solar | DataCuration | Pass | Pass |  | 100
S68113 | Marble Solar | kWandkWh | Pass | Pass |  | 100
S68113 | Marble Solar | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 99.3219
S68113 | Marble Solar | Tracker | Pass | Pass |  | 100
S68113 | Marble Solar | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 98.26896676735629 %, PF: 1 | 98.269
S68113 | Marble Solar | EnergyRatio | Pass | Pass |  | 97.2657
S68113 | Marble Solar | ProductionEnergy | Pass | Pass |  | 100
S68113 | Marble Solar | PVlosses | Pass | Pass |  | 100
S68113 | Marble Solar | PVmodelEnergy24 | Pass | Pass |  | 97.2657
S68113 | Marble Solar | CorrectiveAction | Pass | Pass | All equipment operating normally | 100
S70532 | Longleaf Pine Solar, LLC | Availability | Fail | Fail | Fail: 0.00 % Tracker Controller 1: Availability: 0 % 11 String INV's: Availability: 0 % 12 String INV's: Availability: 0 % INVERTER A10: Availability: 95.65217391304348 % | 0 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H542873', 'hardwareName': 'Tracker Controller 1', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H595369', 'hardwareName': "11 String INV's", 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Availability: \t\t\t 0\t %', 'success': 0.0, 'hardwareKey': 'H595370', 'hardwareName': "12 String INV's", 'isAcknowledged': False}
S70532 | Longleaf Pine Solar, LLC | CheckUpload | Fail | Fail | Tracker Controller 1: Last upload: 6/3/2026 7:25 AM ( US/Eastern ), delay: 5 d 16.2 h | 0 | {'index': 0, 'result': 3, 'detail': 'Last upload: \t\t\t 6/3/2026 7:25 AM\t (\t\t\t US/Eastern\t), delay: \t\t\t 5 d 16.2 h\t', 'success': 0.0, 'hardwareKey': 'H542873', 'hardwareName': 'Tracker Controller 1', 'isAcknowledged': False}
S70532 | Longleaf Pine Solar, LLC | InverterUptime | Fail | Fail | Fail: 0.00 % 12 String INV's: Inverter uptime: 99.6894409937888 % 1 of 40 inverters failed to achieve an uptime of 100 % | 0 | {'index': 0, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 99.6894409937888\t %', 'success': 0.0, 'hardwareKey': 'H595370', 'hardwareName': "12 String INV's", 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': '\t\t\t 1\t of \t\t\t 40\t inverters failed to achieve an uptime of \t\t\t 100\t %', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S70532 | Longleaf Pine Solar, LLC | NetworkCom | Pass | Pass | Pass: 100.00 % INDUSTRIAL COMPUTER - DATALOGGER (SO118811): 27 of 28 TCP devices communicating normally INDUSTRIAL COMPUTER - DATALOGGER (SO118811): 20 of 20 devices on port 1 communicating normally INDUSTRIAL COMPUTER - DATALOGGER (SO118811): 3 of 3 devices on port 4 communicating normally INDUSTRIAL COMPUTER - DATALOGGER (SO118811): 1 of 1 devices on port 2 communicating normally INDUSTRIAL COMPUTER - DATALOGGER (SO118811): 27 of 30 devices on port 0 communicating normally | 100
S70532 | Longleaf Pine Solar, LLC | AlertRecipients | Fail | Fail | Alert email notifications disabled | 0 | {'index': 0, 'result': 3, 'detail': 'Alert email notifications disabled', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S70532 | Longleaf Pine Solar, LLC | CheckHW | Fail | Fail | Fail: 0.00 % 11 String INV's: Inverter group devices that don't receive data should be set to 'Offline'. 12 String INV's: Inverter group devices that don't receive data should be set to 'Offline'. | 0 | {'index': 0, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H595369', 'hardwareName': "11 String INV's", 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': "Inverter group devices that don't receive data should be set to 'Offline'.", 'success': 0.0, 'hardwareKey': 'H595370', 'hardwareName': "12 String INV's", 'isAcknowledged': False}
S70532 | Longleaf Pine Solar, LLC | CheckSysSize | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | DefaultAlerts | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | HasPVmodel | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | HasWSmodel | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | InvalidAlerts | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | SiteConfig | Fail | Fail | Site configured to not generate alert emails | 0 | {'index': 0, 'result': 3, 'detail': 'Site configured to not generate alert emails', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S70532 | Longleaf Pine Solar, LLC | CheckMeterVoltage | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | DataCuration | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | kWandkWh | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | Tracker | Fail | Fail | Fail: 0.00 % Tracker Controller 2: Average tracker error ( Tracker Position TCU 1 ): 5.162712 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 2 ): 5.010487 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 3 ): 5.219921 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 4 ): 5.066218 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 6 ): 5.229388 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 7 ): 5.1355 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 9 ): 5.17971 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 10 ): 5.265781 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 11 ): 5.285481 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 12 ): 5.281296 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 13 ): 5.308228 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 14 ): 5.167063 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 15 ): 5.327059 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 16 ): 5.361785 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 17 ): 5.218068 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 18 ): 5.155914 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 19 ): 5.155129 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 20 ): 5.232318 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 21 ): 5.031975 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 22 ): 5.008597 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 23 ): 5.216853 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 24 ): 5.121782 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 25 ): 5.102134 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 26 ): 5.153339 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 27 ): 5.114405 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 28 ): 5.051635 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 29 ): 5.099558 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 30 ): 5.216917 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 31 ): 5.213085 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 32 ): 5.212649 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 33 ): 64.05043 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 34 ): 5.210495 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 35 ): 5.185285 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 36 ): 5.39419 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 37 ): 5.260386 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 38 ): 5.297767 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 39 ): 5.319089 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 40 ): 5.236355 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 41 ): 5.006546 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 42 ): 5.22219 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 43 ): 5.230725 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 44 ): 5.219262 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 45 ): 5.227262 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 46 ): 5.045512 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 47 ): 5.051118 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 48 ): 5.099733 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 49 ): 5.232605 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 50 ): 5.270871 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 51 ): 5.038798 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 52 ): 5.172347 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 53 ): 5.168454 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 54 ): 5.027005 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 55 ): 5.190786 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 57 ): 5.230815 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 58 ): 5.171702 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 59 ): 5.248775 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 60 ): 5.172385 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 62 ): 5.127875 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 63 ): 5.1334 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 64 ): 5.137572 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 65 ): 5.219288 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 66 ): 5.031323 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 67 ): 5.179514 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 68 ): 5.296859 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 69 ): 5.171233 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 70 ): 5.233246 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 71 ): 5.135944 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 72 ): 5.142511 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 73 ): 5.337718 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 74 ): 5.03545 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 75 ): 5.071803 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 76 ): 5.037499 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 77 ): 5.15371 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 78 ): 5.204083 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 79 ): 5.173408 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 80 ): 5.122581 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 81 ): 5.111313 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 82 ): 5.192276 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 83 ): 5.235321 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 84 ): 5.339651 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 85 ): 5.114261 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 86 ): 5.038347 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 87 ): 5.130798 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 88 ): 5.260382 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 89 ): 5.130189 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 90 ): 5.212576 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 91 ): 5.24976 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 92 ): 5.151194 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 93 ): 5.117936 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 94 ): 5.296285 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 95 ): 5.219744 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 96 ): 5.068168 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 98 ): 5.320112 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 99 ): 5.28538 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 100 ): 5.165229 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 101 ): 5.270815 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 102 ): 5.15836 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 103 ): 5.193865 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 104 ): 5.075851 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 105 ): 5.27428 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 106 ): 5.201046 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 108 ): 5.140089 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 109 ): 5.214223 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 110 ): 5.109879 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 111 ): 5.24436 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 112 ): 5.233431 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 113 ): 5.075376 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 114 ): 5.21564 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 115 ): 5.213276 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 116 ): 5.209072 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 117 ): 5.189354 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 118 ): 5.226066 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 119 ): 5.170258 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 120 ): 5.289508 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 121 ): 5.003202 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 123 ): 5.134264 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 124 ): 5.353782 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 125 ): 5.216372 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 126 ): 5.214128 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 127 ): 5.248924 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 128 ): 5.314049 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 129 ): 5.102187 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 130 ): 5.26114 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 131 ): 5.17277 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 132 ): 5.204338 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 133 ): 5.222102 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 134 ): 5.216518 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 136 ): 5.106381 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 137 ): 5.285847 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 138 ): 5.348536 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 139 ): 5.210716 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 140 ): 5.167895 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 141 ): 5.136137 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 142 ): 5.072047 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 143 ): 5.269969 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 144 ): 5.150686 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 145 ): 5.015624 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 146 ): 5.157609 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 147 ): 5.107089 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 148 ): 5.105285 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 149 ): 5.043522 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 150 ): 5.134199 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 151 ): 5.270627 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 152 ): 5.134162 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 153 ): 5.147308 degrees Tracker Controller 2: Average tracker error ( Tracker Position TCU 154 ): 5.309813 degrees | 0 | {'index': 0, 'result': 3, 'detail': 'Average tracker error (\t\t\t Tracker Position TCU 1\t): \t\t\t 5.162712\t degrees', 'success': 0.0, 'hardwareKey': 'H542874', 'hardwareName': 'Tracker Controller 2', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': 'Average tracker error (\t\t\t Tracker Position TCU 2\t): \t\t\t 5.010487\t degrees', 'success': 0.0, 'hardwareKey': 'H542874', 'hardwareName': 'Tracker Controller 2', 'isAcknowledged': False}, {'index': 2, 'result': 3, 'detail': 'Average tracker error (\t\t\t Tracker Position TCU 3\t): \t\t\t 5.219921\t degrees', 'success': 0.0, 'hardwareKey': 'H542874', 'hardwareName': 'Tracker Controller 2', 'isAcknowledged': False}
S70532 | Longleaf Pine Solar, LLC | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.61580210344066 %, PF: 0.980000003315249 | 99.6158
S70532 | Longleaf Pine Solar, LLC | ProductionEnergy | Pass | Pass |  | 100
S70532 | Longleaf Pine Solar, LLC | CorrectiveAction | Fail | Fail | Equipment repair required. Low availability , Solar tracker, Inverter group : Tracker Controller 1, 11 String INV's, 12 String INV's | 50 | {'index': 0, 'result': 3, 'detail': "Equipment repair required. \t\t\t Low availability\t, \t\t\t Solar tracker, Inverter group\t: \t\t\t Tracker Controller 1, 11 String INV's, 12 String INV's\t", 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S70645 | Williams Solar, LLC | Availability | Fail | Fail | INVERTER A20: Availability: 21.153846153846153 % | 21.1538 | {'index': 0, 'result': 3, 'detail': 'Availability: \t\t\t 21.153846153846153\t %', 'success': 0.21153846153846154, 'hardwareKey': 'H543196', 'hardwareName': 'INVERTER A20', 'isAcknowledged': False}
S70645 | Williams Solar, LLC | CheckUpload | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | InverterUptime | Fail | Fail | Fail: 0.00 % 11 String Inverters: Inverter uptime: 97.2811671087533 % 1 of 40 inverters failed to achieve an uptime of 100 % | 0 | {'index': 0, 'result': 3, 'detail': 'Inverter uptime: \t\t\t 97.2811671087533\t %', 'success': 0.0, 'hardwareKey': 'H595270', 'hardwareName': '11 String Inverters', 'isAcknowledged': False}, {'index': 1, 'result': 3, 'detail': '\t\t\t 1\t of \t\t\t 40\t inverters failed to achieve an uptime of \t\t\t 100\t %', 'success': 0.0, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}
S70645 | Williams Solar, LLC | NetworkCom | Pass | Pass | Pass: 100.00 % INDUSTRIAL COMPUTER - DATALOGGER: 28 of 28 TCP devices communicating normally INDUSTRIAL COMPUTER - DATALOGGER: 20 of 20 devices on port 1 communicating normally INDUSTRIAL COMPUTER - DATALOGGER: 1 of 1 devices on port 4 communicating normally INDUSTRIAL COMPUTER - DATALOGGER: 2 of 2 devices on port 3 communicating normally INDUSTRIAL COMPUTER - DATALOGGER: 1 of 1 devices on port 2 communicating normally | 100
S70645 | Williams Solar, LLC | AlertRecipients | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | CheckHW | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | CheckSysSize | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | DefaultAlerts | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | HasPVmodel | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | HasWSmodel | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | InvalidAlerts | Fail | Fail | INVERTER A20: Alert ' Sungrow Inverter Fault Alert ' triggered 25 times in the past 24 hours. | 0 | {'index': 0, 'result': 3, 'detail': "Alert '\t\t\t Sungrow Inverter Fault Alert\t' triggered \t\t\t 25\t times in the past 24 hours.", 'success': 0.0, 'hardwareKey': 'H543196', 'hardwareName': 'INVERTER A20', 'isAcknowledged': False}
S70645 | Williams Solar, LLC | SiteConfig | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | CheckMeterVoltage | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | CheckWeather | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | DataCuration | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | kWandkWh | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | PVPMenergy | Pass | Pass | METER - PRODUCTION: Inverter / meter energy correlation: % | 97.4621
S70645 | Williams Solar, LLC | CheckPMCTs | Pass | Pass | METER - PRODUCTION: Phase current ratio 99.28812888736319 %, PF: 0.980000003315249 | 99.2881
S70645 | Williams Solar, LLC | EnergyRatio | Fail | Fail | INVERTER A20: Low energy ratio: 0 | 0 | {'index': 0, 'result': 3, 'detail': 'Low energy ratio: \t\t\t 0\t', 'success': 0.0, 'hardwareKey': 'H543196', 'hardwareName': 'INVERTER A20', 'isAcknowledged': False}
S70645 | Williams Solar, LLC | ProductionEnergy | Pass | Pass |  | 100
S70645 | Williams Solar, LLC | PVlosses | Fail | Fail | INVERTER A20: Downtime loss detected: 77.78479836569196 % ( 1030.240788 kWh) | 0 | {'index': 0, 'result': 3, 'detail': 'Downtime loss detected: \t\t\t 77.78479836569196\t % (\t\t\t 1030.240788\t kWh)', 'success': 0.0, 'hardwareKey': 'H543196', 'hardwareName': 'INVERTER A20', 'isAcknowledged': False}
S70645 | Williams Solar, LLC | PVmodelEnergy24 | Pass | Pass |  | 94.8742
S70645 | Williams Solar, LLC | CorrectiveAction | Fail | Fail | Corrective action recommended, ( kWh/day loss). | 50 | {'index': 0, 'result': 3, 'detail': 'Corrective action recommended, ( kWh/day loss). ', 'success': 0.5, 'hardwareKey': '', 'hardwareName': '', 'isAcknowledged': False}

## Failing Sites
Site Key | Site Name | Failing Rules | Weather | Run At
S40834 | Green Elementary | InvalidAlerts; CheckWeather; DataCuration | 2 | 2026-06-08T21:55:02Z
S40835 | Gallia Academy | Availability; CheckUpload; InverterUptime; InvalidAlerts; PVlosses | 2 | 2026-06-08T06:51:25Z
S40836 | Rio Grande Elementary | InvalidAlerts; CheckWeather; DataCuration | 2 | 2026-06-08T13:59:46Z
S44485 | RRH 1 & 2 | Availability; AlertRecipients; SiteConfig; CorrectiveAction | 1 | 2026-06-08T09:42:46Z
S44566 | RIT | CheckHW; EnergyRatio | 1 | 2026-06-09T00:57:17Z
S44882 | Monroe Landfill | Availability; InverterUptime; DefaultAlerts; DataCuration; EnergyRatio (+2 more) | 1 | 2026-06-09T00:21:58Z
S51957 | WCPS - William Perry Elementary School | InverterUptime; EnergyRatio; PVlosses; PVmodelEnergy24 | 1 | 2026-06-08T20:45:58Z
S51958 | WCPS - Westwood Hills Elementary School | CheckHW; DefaultAlerts | 1 | 2026-06-08T21:43:06Z
S51959 | WCPS - Waynesboro High School | CheckHW; DefaultAlerts; EnergyRatio; PVlosses; PVmodelEnergy24 | 2 | 2026-06-08T16:38:57Z
S51960 | WCPS - Kate Collins Middle School | CheckHW; DefaultAlerts; EnergyRatio; PVlosses; PVmodelEnergy24 | 1 | 2026-06-08T22:21:45Z
S54553 | Butler Maple | DefaultAlerts | 2 | 2026-06-08T17:00:11Z
S54613 | Warbler | Availability; InverterUptime | 2 | 2026-06-08T22:14:01Z
S54681 | Eagle | Availability; CheckUpload; NetworkCom; CheckHW; InvalidAlerts (+6 more) | 2 | 2026-06-08T14:33:56Z
S55935 | Manuel Lawrence Dairy | Availability; DefaultAlerts; CheckWeather; EnergyRatio; PVlosses (+1 more) | 1 | 2026-06-08T10:05:24Z
S59656 | Whitetail | Availability; CheckUpload; CheckHW; InvalidAlerts; CheckWeather (+2 more) | 1 | 2026-06-08T09:15:11Z
S63837 | Bulloch 1B | CheckUpload; DefaultAlerts; Tracker | 2 | 2026-06-08T08:43:29Z
S63838 | Bulloch 1A | DefaultAlerts; Tracker | 1 | 2026-06-08T18:36:13Z
S63839 | Richmond | Availability; CheckHW; DefaultAlerts; Tracker; EnergyRatio (+1 more) | 2 | 2026-06-09T00:58:51Z
S63840 | Upson | DefaultAlerts; CheckWeather; CheckPMCTs | 2 | 2026-06-09T03:50:49Z
S64602 | McLean | Availability; CheckUpload; CheckHW; DefaultAlerts; InvalidAlerts (+3 more) | 1 | 2026-06-08T14:32:54Z
S64603 | Shorthorn | Availability; CheckUpload; CheckHW; DefaultAlerts; Tracker (+1 more) | 1 | 2026-06-08T23:14:06Z
S65784 | Washington Solar | Availability; CheckHW; DefaultAlerts; DataCuration; Tracker (+2 more) | 1 | 2026-06-08T12:44:54Z
S65785 | Harding Solar | Availability; CheckHW; DefaultAlerts; Tracker; PVlosses (+1 more) | 2 | 2026-05-29T06:08:36Z
S65786 | Whitehall Solar | Availability; DefaultAlerts; CheckWeather; Tracker | 2 | 2026-05-26T06:02:47Z
S65787 | Sunflower Solar | DefaultAlerts; CheckWeather; Tracker; EnergyRatio; PVmodelEnergy24 | 1 | 2026-06-08T17:31:09Z
S65788 | Gray Fox Solar | Availability; CheckUpload; InverterUptime; DefaultAlerts; Tracker (+2 more) | 1 | 2026-06-01T05:58:41Z
S65918 | C & B Graham Energy | Availability; CheckUpload; NetworkCom; CheckHW; DefaultAlerts (+8 more) | 2 | 2026-06-08T17:47:17Z
S66000 | Auburn Solar | CheckWeather | 3 | 2026-06-08T18:36:02Z
S66001 | Sheridan Solar | CheckWeather | 2 | 2026-06-08T19:56:57Z
S66930 | Elk Solar | Availability; CheckUpload; InverterUptime; CheckHW; CheckMeterVoltage (+7 more) | 2 | 2026-06-08T08:46:08Z
S68112 | Wallace Solar | CheckWeather; EnergyRatio | 2 | 2026-05-26T05:56:41Z
S70532 | Longleaf Pine Solar, LLC | Availability; CheckUpload; InverterUptime; AlertRecipients; CheckHW (+3 more) | 5 | 2026-06-09T03:37:29Z
S70645 | Williams Solar, LLC | Availability; InverterUptime; InvalidAlerts; EnergyRatio; PVlosses (+1 more) | 2 | 2026-06-08T08:32:26Z

## Raw Sample
First site raw JSON (for exploration):
{
"key": "S40834",
"name": "Green Elementary",
"passed": 20,
"runAt": "2026-06-08T21:55:02Z",
"lastChanged": "2026-06-08T21:55:07Z",
"weatherCondition": 2,
"status": 8,
"results": [
{
"id": "Availability",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "CheckUpload",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "DataUsage",
"result": 1,
"show": false,
"detail": "",
"success": "NaN",
"errors": []
},
{
"id": "InverterUptime",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "NetworkCom",
"result": 4,
"show": true,
"detail": "Pass: 100.00 %\rPowerLogger 1000: \t\t\t 3\t of \t\t\t 3\t devices on port \t\t\t 2\t communicating normally\rPowerLogger 1000: \t\t\t 11\t of \t\t\t 11\t devices on port \t\t\t 1\t communicating normally",
"success": 100.0,
"errors": []
},
{
"id": "AlertRecipients",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "CheckHW",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "CheckSysSize",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "DefaultAlerts",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "HasPVmodel",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "HasWSmodel",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "InvalidAlerts",
"result": 3,
"show": true,
"detail": "Site alert '\t\t\t Rule Tool Alert\t' (\t\t\t 126379653\t) doesn't have an active configuration.",
"success": 0.0,
"errors": [
{
"index": 0,
"result": 3,
"detail": "Site alert '\t\t\t Rule Tool Alert\t' (\t\t\t 126379653\t) doesn't have an active configuration.",
"success": 0.0,
"hardwareKey": "",
"hardwareName": "",
"isAcknowledged": false
}
]
},
{
"id": "SiteConfig",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "CheckMeterVoltage",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "CheckWeather",
"result": 3,
"show": true,
"detail": "Weather Station (Standard): No change in ambient temperature",
"success": 0.0,
"errors": [
{
"index": 0,
"result": 3,
"detail": "No change in ambient temperature",
"success": 0.0,
"hardwareKey": "H119161",
"hardwareName": "Weather Station (Standard)",
"isAcknowledged": false
}
]
},
{
"id": "DataCuration",
"result": 3,
"show": true,
"detail": "Weather Station (Standard): The value \"\t\t\t Ambient temp\t\" (\t\t\t TempF\t) is stuck at \t\t\t -20.200\t \t\t\t \u00b0F\t.",
"success": 100.0,
"errors": [
{
"index": 0,
"result": 3,
"detail": "The value \"\t\t\t Ambient temp\t\" (\t\t\t TempF\t) is stuck at \t\t\t -20.200\t \t\t\t \u00b0F\t.",
"success": 1.0,
"hardwareKey": "H119161",
"hardwareName": "Weather Station (Standard)",
"isAcknowledged": false
}
]
},
{
"id": "kWandkWh",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "PVPMenergy",
"result": 4,
"show": true,
"detail": "Elkor MKII Production Meter: Inverter / meter energy correlation: %",
"success": 97.66374454804765,
"errors": []
},
{
"id": "Tracker",
"result": 1,
"show": false,
"detail": "",
"success": "NaN",
"errors": []
},
{
"id": "CheckPMCTs",
"result": 4,
"show": true,
"detail": "Elkor MKII Production Meter: Phase current ratio \t\t\t 98.16743905668737\t %, PF: \t\t\t 0.9967669907722094\t",
"success": 98.16743905668737,
"errors": []
},
{
"id": "EnergyRatio",
"result": 4,
"show": true,
"detail": "",
"success": 76.11583372395667,
"errors": []
},
{
"id": "ProductionEnergy",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "PVlosses",
"result": 4,
"show": true,
"detail": "",
"success": 100.0,
"errors": []
},
{
"id": "PVmodelEnergy24",
"result": 4,
"show": true,
"detail": "",
"success": 87.08311660951708,
"errors": []
},
{
"id": "CorrectiveAction",
"result": 4,
"show": true,
"detail": "All equipment operating normally",
"success": 100.0,
"errors": []
}
],
"loss": 0.0
}