## Site Emails
Date | From / Participants | Subject | Site(s) | Category | WO / Ref # | Key Dates | Status / Next Action | Contents | Gmail link
2026-06-24 | Steve Maloney (SolRiver) ↔ Ayaz Kiani (Carolina Solar Services) | CSS / SolRiver O&M — DC wire theft | Elk Solar (Raeford, NC) | O&M / Theft | — | First theft 5/27/26; ongoing | CSS site visit ~6/26 for DC-wire replacement quote; fence-repair quote pending | DC string wire stolen across the array (~100 runs); of 43 inverters only ~10 online. Fencing also stolen/damaged. SolRiver requested urgent CSS site visit + repair quote and sent theft photos, as-builts, and AlsoEnergy screenshots. CSS developing a dispatch plan. | Open thread
2026-06-24 | Steve Maloney / Abhinav Korni (SolRiver) ↔ Jayme Orrock (NARENCO) | SR/NRCO — Elk Inverters Offline / Not Communicating | Elk Solar (Raeford, NC) | O&M / Theft | — | Pad 1 down by 6/12; 35/43 off 6/18; 3 op. 6/23 | NARENCO truck rolls 'non-covered' until fence repaired; overnight patrol being hired | Inverters offline from DC-wire theft: 35 of 43 offline by 6/18, ~10 online 6/22, only 3 operational morning of 6/23; 47 rows vandalized. NARENCO techs dispatched 5/28–6/23 restored some strings. Gate code provided to techs. | Open thread
2026-06-24 | Steve Maloney (SolRiver) ↔ George Porter (Investigate NC) | Site security / overnight patrol | Elk Solar (547 McLaughlin Rd, Raeford, Hoke Co. NC) | Security | — | Site assessment 6/11; redline 6/24 | Contract (in name of Elk Solar LLC, signed by CEO B. Conard) in redline 6/24; start date TBD | Security procurement after repeated theft. Investigate NC did a 6/11 assessment (drone, perimeter, sheriff reports) and proposed 24/7 guard; SolRiver scoped to overnight only (8pm–6am), short-term, terminable at will. | Open thread
2026-06-23 | omops via Projects (NARENCO / NCC) | NARENCO O&M ¦ 06/23/26 Incident Report | Washington Solar; Whitetail | Grid / Utility | WO 50396; WO 50397 | 6/22–6/23 | Restored remotely by NCC; no action | Utility-caused trips. WO 50396 Washington: tripped 6/22 19:21, restored 6/23 09:00. WO 50397 Whitetail: tripped 6/23 15:15, restored 6/23 15:45. | Open thread
2026-06-19 | omops via Projects (NARENCO / NCC) | NARENCO O&M ¦ 06/19/26 Incident Report | Elk; Sunflower; Williams Solar | Grid / Utility | WO 50379; 50380; 50381 | 6/18–6/19 | Restored remotely by NCC; no action | Utility trips restored remotely. WO 50379 Elk: 6/18 19:45 → 6/19 07:15. WO 50380 Sunflower: 6/18 20:30 → 6/19 07:15. WO 50381 Williams: 6/18 20:30 → 6/19 07:15. | Open thread
2026-06-17 | omops via Projects (NARENCO / NCC) | NARENCO O&M ¦ 06/17/26 Incident Report | Whitetail | Grid / Utility | WO 50366 | 6/17 | Restored remotely by NCC; no action | WO 50366 Whitetail: site tripped offline 6/17 04:30; production restored remotely by NCC 6/17 08:30. | Open thread
2026-06-17 | Steve Maloney (SolRiver) ↔ Brenna Franzman (Casey Electric) | Whitetail DAS / fiber review | Whitetail (Tell City / Danville, IN) | DAS / Comms | — | Site visit + calls 6/11–6/24 | Casey recommends full DAS replacement; repair-vs-replace decision pending | Field DAS doesn't match drawings: missing fiber between cabinets, no cell modem, unterminated/unlabeled wiring; Solectria XGI 1500 inverters (need VPN). Casey recommends replacing the DAS rather than tracing it. Also discussing Solectria thermal/neutral-conductor inverter failures and a Padcom float-controller fix. | Open thread
2026-06-19 | Steve Maloney (SolRiver) ↔ Ken Wilson / Ben Furrer (Sargent Electric) | SolRiver Capital Danville IN DAS Rework | Whitetail / Danville, IN | DAS / Comms | — | Proposal 6/16; revised T&M 6/19 | Sargent needs a PO before scheduling; earliest tech ~Mon 6/29 | Sargent to assess installed DAS vs plan sets. Proposal sent 6/16, revised T&M scope 6/19. No work performed yet. | Open thread
2026-06-16 | Steve Maloney (SolRiver) ↔ Jack Stringer (Stem / AlsoEnergy) | DAS modem / cell-plan BOM | Whitetail | DAS / Comms | — | 6/15–6/16 | Needs PO / signed quote to assign a PM | Stem proposed adding a modem/cell plan (with VPN) to the main DAS (WT200) + exterior antenna; flags the Solectria gateway may not fit the AlsoEnergy enclosure. Quote includes ~12 hrs PM + remote re-commissioning of the DAS units. | Open thread
2026-06-17 | Steve Maloney (SolRiver) ↔ Chuck 'Charllie' Joyce (Hendricks Power Coop) | Transformer spec sheets | Whitetail / Danville, IN | O&M / Equipment | 2,500 kVA 3-ph xfmrs | 6/16–6/17 | Specs + nameplate photos received; closed | SolRiver was missing technical specs for installed transformers. Hendricks Power supplied the spec sheet (standard 2,500 kVA 3-phase distribution transformers) plus nameplate photos for each installed unit. | Open thread
2026-06-16 | Bryan Focht / Alix Lefler (Portland General Electric) ↔ John Brown / Riley Sullivan (SolRiver) | Wallace Solar: Allowed to operate at full capacity | Wallace Solar (6475 Wallace Rd NW, Salem, OR) | Grid / Utility | — | Orig. test Mar 2025; revived 6/16 | Provide PGE a contact + remote SEL-relay access for diagnostics | Older PGE thread (Mar 2025 MBTT/transfer-trip test cleared the site to full capacity) revived 6/16; PGE's Bryan Focht is locating the right contact and asking whether SolRiver has remote access to the on-site SEL relay to aid diagnostics. | Open thread
2026-06-15 | Steve Maloney (SolRiver) ↔ Jayme Orrock (NARENCO); memo from Trent Miller (Duke Energy) | Elk Solar — Smart Inverter Pilot — Need Volt-VAR Enabled | Elk Solar (Duke territory, NC) | Grid / Utility | Duke Smart Inverter Pilot | Duke memo 6/8; SR follow-up 6/15 | NARENCO engaging Aderis to re-enable volt-VAR/volt-Watt | After Elk returned to normal circuit arrangement and the 2 MW limit was removed, volt-VAR/volt-Watt is not enabled, causing over-voltage from reactive-power under-absorption (site may still be in constant power-factor mode). Duke requests re-enabling volt-VAR/volt-Watt. | Open thread
2026-06-16 | Duke Energy — Grid Integration / Generator Testing & Performance (GTP); fwd internally by B. Conard / R. Sullivan | Duke Energy Memorandum: IEEE 1547-2018 Compliance — Ride-Through Settings Implementation | All Duke-interconnected SolRiver DER (NC) | Grid / Utility | Memo PDF (fwds: 19ed1081…, 19ed24da…) | Compliance deadline 7/1/2027 | Long-term task: update site voltage/freq ride-through settings on POI reclosers | Duke is updating voltage/frequency ride-through on utility-owned POI reclosers and requires all DER customers to update their own site settings to match for IEEE 1547-2018 compliance by 7/1/2027. Duke will send per-facility reminders as each POI recloser is updated. Brandon flagged it for the long-term task list. Specific setting values are in the attached PDF. | Open thread
2026-06-15 | Tracy Beaudoin (Travelers) / Abhinav Korni (SolRiver) / Dawn Cruz (Marsh) | Solar loss at Graham Project | C&B Graham Energy | Insurance | Claim# F7Q1033; Marsh# 26NYC590490; DOL 2/15/26 | Loss 2/15/26; follow-up 6/10; reply 6/15 | RCA still ongoing; SolRiver to submit RCA + supporting docs | Equipment-loss claim (DOL 2/15/26) involving Solectria inverters. Travelers requested pre-incident O&M reports, alarm logs, work orders, all Solectria communications, warranty/claims docs, and a root cause report. Abhinav replied 6/15 the RCA is not yet finalized. | Open thread
2026-06-16 | Steve Maloney / Brandon Conard (SolRiver) ↔ Ralph Lewis (landowner) | Green Solar CUP citation (water / screening) | Green Solar | Land / County / Tax | County CUP citation | Hearing scheduled then cancelled | Resolving water-availability + screening with county; ongoing | County conditional-use-permit citation. Site is non-irrigated with no domestic water on-site; landowner offered his own supply ~1,000 ft away / a neighbor. Fence screening considered to satisfy the county (ties to Konisto CO). County hearing cancelled; SolRiver actively resolving. | Open thread
2026-06-17 | Steve Maloney (SolRiver) ↔ Michael Jackson (Konisto) | Green — fence screening change order | Green Solar / Green Elementary | Land / County / Tax | Change order (amount in thread) | 2–4 wk lead from approval | Pending county approval; Konisto will NOT warranty the work | Fence-screening change order: screening fabric on 400 ft of fence line north of the entrance, with wind-relief holes recommended. 2–4 weeks to procure/install once approved. | Open thread
2026-06-24 | Bette Anne Mellentine (NARENCO) → SolRiver (Conard, Maloney, projects@) | Richmond Cadle Pay App #12 — Final | Richmond (Richmond County S2, GA) | Construction | Pay App #12 (final) | Final completion 6/24; final inspection 6/22 | SolRiver to review/process final pay app | NARENCO submitted the final closeout: Pay App #12 with Final Lien Waiver, Final Completion Certificate (6/24/26), email to GA EPD for NOT submission, and Final Inspection Letter. Indicates project final completion. | Open thread
2026-06-12 | Steve Maloney (organizer); Sargent (Wilson, Friday, Guess); SolRiver (Korni, Conard, Jones) | Invitation: SolRiver/Sargent — Indiana DAS call | Whitetail / Indiana | DAS / Comms | — | Call 6/12 3:00 pm MDT | Coordination call held; feeds the DAS-rework effort | 30-minute DAS coordination call between SolRiver and Sargent Electric regarding the Indiana site DAS rework (calendar invite / meet link). | Open thread
2026-06-15 | Ken Wilson (Sargent Electric) ↔ Steve Maloney | Follow-up — Indiana DAS | Whitetail / Indiana | DAS / Comms | — | 6/15 | Scheduling the Indiana DAS discussion | Sargent following up to schedule the Indiana DAS discussion (same DAS-rework effort). | Open thread
2026-06-24 | Abhinav Korni (SolRiver) → M-RETS admin | M-RETS — Request to Correct Reporting Period End Dates | Shorthorn (M15837); Washington Solar (M17730) | Regulatory / REC | Gen M15837, M17730 | 6/24 | Requested M-RETS correct end dates; awaiting process | Shorthorn shown 1/6–2/2/26 should be 1/6–2/3/26; Washington shown 2/1–3/28/26 should be 2/1–2/28/26. Affects REC reporting accuracy. | Open thread
2026-06-15 | M-RETS (systemadmin) → John Brown (SolRiver) | M-RETS — Issuance Report (Elk Solar) | Elk Solar (Gen M16408, NC) | Regulatory / REC | M16408; 415 (Apr) + 752 (May) RECs | Vintages 04/2026 & 05/2026; issued 6/15 | Issued to SolRiver 'Default' account; informational | M-RETS issued Elk Solar RECs: 415 for the April 2026 vintage and 752 for the May 2026 vintage, into SolRiver Capital, LLC (MM2265). | Open thread
2026-06-15 | PJM-EIS GATS (auto) → projects@ | PJM-EIS GATS — Acct#41498 — Gallipolis Solar River LLC — Generation | Gallia Academy (Gallipolis, OH) | Regulatory / REC | NON217675; Acct#41498; 51,691 kWh | May 2026; entered 6/15 | Logged in GATS; informational | GATS confirmation that 51,691 kWh of May 2026 solar generation was added for the Gallia Academy unit (Meter #1 26,065 kWh + Meter #2 25,626 kWh, both read 05/31/2026). | Open thread
2026-06-19 | Wendy Garduno (SolRiver) ↔ Jack MacMaster (Nelson Mullins); county: R. Fisher, D. Crumley | Re: Bulloch County Assessment Appeals | Bulloch 1A & 1B (Bulloch Co., GA) | Land / County / Tax | FMV $6.8M (audit) vs $2.7M (notices); appeal ack 6/1 | Notices 5/22; certified assessment due 7/15 | Nelson Mullins setting appeal strategy; county audit responses in ~2 wks | Conflicting valuations: the April audit pegged each site at ~$6.8M FMV while May notices show ~$2.7M each. Income-method argument (favored by SolRiver) apparently not addressed in the re-assessment. County confirmed the audit wave targeted solar projects. | Open thread
2026-06-18 | Wendy Garduno (SolRiver) → Alex Krone (Live Oak Bank) | Re: Gallipolis Solar River Q1 2026 Financials and Production | Gallia Academy (Gallipolis, OH) | Regulatory / REC | Q1 2026 lender report | Q1 2026 (Jan–Mar) | Report delivered; implement winter snow-management plan | Live Oak Bank requested Q1 2026 financials + production for Gallipolis. Wendy explained Jan/Feb production was lowered by heavy snow cover and the team will implement a snow management plan for winter. | Open thread
2026-06-18 | Georgia Power (do-not-reply) → projects@ | Outage New — 92 Ben-Hill Rd | GA site (92 Ben-Hill Rd) | Grid / Utility | — | 6/18 7:41 PM; no ETA | Automated outage notice; monitor | Georgia Power reported widespread outages affecting 92 Ben-Hill Rd with no estimated restoration time. | Open thread
2026-06-13 | Georgia Power (do-not-reply) → projects@ | Outage New — 2436 GA-Hwy-88 | GA site (2436 GA-Hwy-88) | Grid / Utility | — | 6/13 2:48 PM; restore ~5:00 PM | Automated outage notice; monitor | Georgia Power reported an outage at 2436 GA-Highway-88 with anticipated restoration by 06/13 05:00 PM. | Open thread
2026-06-22 | Steve Maloney / Brandon Conard (SolRiver) ↔ Oregon CSP (J. Siegel, M. Larson) / Energy Solutions (S. Lauer) | Re: Annual Reconciliation Notice (oversubscription fee) | Oregon CSP / Canyonville Solar (OR) | Regulatory / REC | $15,247.38; OR PUC Order 26-180 | Method eff 5/27; response due 6/19; deferred to 7/8 billing | PA rejected lump-sum redistribution; SolRiver to find another method | New OR PUC reconciliation requires oversubscribed participants to repay the utility. SolRiver chose to cover the fees and proposed a single $15,247.38 payment for redistribution, but the PA said it can't redistribute lump-sum funds, so the mechanism was rejected. | Open thread
2026-06-02 | Wendy Garduno (SolRiver) ↔ Lisa Hawley (Douglas County, OR planner) | Fwd: SR/Douglas County — Canyonville Solar | Canyonville Solar (N. Gazley Rd, Myrtle Creek, OR) | Land / County / Tax | Approval Condition #4 (decommissioning MOU) | Permit extension ~3/25; MOU drafting Jun | Provide entity/signer details so county can draft the MOU | To satisfy Condition #4, the county wants a decommissioning MOU (modeled on a Linn County agreement). SolRiver provided the decommissioning report/site plan; the county needs corporate name, ATTN, address, email, and authorized signer to draft the MOU. | Open thread
2026-06-17 | Oregon CSP (M. Larson) → skylar@ (former); fwd by B. Conard | Fwd: Certification Deadline Approaching — Canyonville 1 and 2 | Canyonville Solar 1 & 2 (OR) | Regulatory / REC | Ticket 15663:1176751 | Certification deadline 6/26/2026 | Draft extension request (4 required points) or certify before 6/26 | OR CSP warned that Canyonville 1 & 2's certification deadline (6/26) is near and laid out extension-letter requirements. Brandon directed the team to start drafting a response. | Open thread
2026-06-18 | Donna DuRant Winchester (landowner) ↔ Steve Maloney (SolRiver) | SC Property Tax return — DuRant Farm Solar (Timmonsville, SC) | DuRant Farm Solar (Timmonsville, SC) | Land / County / Tax | SC DOR PT-300 | SolRiver filed PT-300 Feb 2026 | Confirm to landowner; resolve possible filing disconnect | Landowner forwarded an SC DOR property-tax notice; after speaking with SC DOR she says both landowner and SolRiver must file separately. Steve replied SolRiver already filed its PT-300 in February with no state disputes. | Open thread
2026-06-24 | Vonda Hutchinson (Waynesboro City Public Schools, VA) → Matt La Rocca (SolRiver) | Re: Waynesboro/SolRiver: Renewable Energy Credit Transfers | WCPS — Waynesboro City Public Schools (VA) | Regulatory / REC | Remaining ~20% RECs; via SSA amendment | Thread Jan–Jun; decision 6/24 | Waynesboro agreed if no fee; SolRiver to execute transfer (SSA amendment) | SolRiver held Waynesboro's remaining RECs and proposed amending the SSA so the remaining 20% of RECs (existing + future) transfer to SolRiver. Waynesboro agreed provided there is no fee to them. | Open thread

## Filtered Out (no site)
Date | From / Subject | Category | Note | Gmail link
2026-06-24 | ChatGPT — find products from an image | Ad / Promo | OpenAI marketing | Open thread
2026-06-24 | Altvia — IR event highlights | Newsletter | Vendor newsletter | Open thread
2026-06-24 | Anna Dillbeck — consultant waiting | Recruiter | Staffing outreach | Open thread
2026-06-23 | Verizon 5G Business Internet | Ad / Promo | Telecom marketing | Open thread
2026-06-23 | Nodal — June 2026 newsletter | Newsletter | Market newsletter | Open thread
2026-06-23 | Renewable procurement sessions — register by 6/30 | Ad / Promo | Conference promo | Open thread
2026-06-23 | Fundraising Readiness Checklist | Ad / Promo | Marketing | Open thread
2026-06-23 | Seraphim USA — Domestic Content panels | Vendor | Panel-supply sales | Open thread
2026-06-23 | Simplifile — credit card surcharge change | Admin | Billing notice | Open thread
2026-06-23 | Colorado SoS — Periodic Report (Korsolis LLC) | Admin | Entity filing reminder | Open thread
2026-06-23 | ChatGPT — turn notes into a draft | Ad / Promo | OpenAI marketing | Open thread
2026-06-23 | IDR — expert network invite | Recruiter | Expert-network outreach | Open thread
2026-06-23 | Chicago Title — form 6s | Admin | Title/closing admin | Open thread
2026-06-23 | Film crowdfunding pitch | Ad / Promo | Solicitation | Open thread
2026-06-22 | Privacy Policy update | Admin | Policy notice | Open thread
2026-06-22 | Anna — recruiter intro to Matt | Recruiter | Staffing outreach | Open thread
2026-06-22 | Working capital loan pitch | Ad / Promo | Lending solicitation | Open thread
2026-06-22 | Climatize — idle balances pitch | Ad / Promo | Fintech solicitation | Open thread
2026-06-22 | CJR Renewables — Intersolar invite | Ad / Promo | Event marketing | Open thread
2026-06-18 | EIA 860/923 — contact change (Matt LaRocca) | Regulatory | Reporting-contact admin | Open thread
2026-06-18 | Identity Services — brand protection | Ad / Promo | Marketing | Open thread
2026-06-18 | EIA-860 May report overdue | Regulatory | Filing reminder (fleet-wide) | Open thread
2026-06-18 | PGE business feedback survey | Ad / Promo | Utility survey | Open thread
2026-06-17 | Newsletter — closing faster | Newsletter | Industry newsletter | Open thread
2026-06-17 | PEI — AI webinar | Ad / Promo | Webinar promo | Open thread
2026-06-16 | DEQ / AccessDEQ — password resets & OTP (5 msgs) | Auth | NC DEQ portal auth | Open thread
2026-06-16 | CCEBA — Duke NC IRP court update | Industry | Policy update | Open thread
2026-06-16 | EIA-860 overdue (Matt / Brandon) | Regulatory | Filing reminder | Open thread
2026-06-16 | PR Newswire — media monitoring pitch | Ad / Promo | Sales | Open thread
2026-06-16 | Spencer Ogden — consultant waiting | Recruiter | Staffing outreach | Open thread
2026-06-16 | Oregon CSP — PA compliance extension to 6/30 | Regulatory | Related to Oregon CSP (site sheet) | Open thread
2026-06-15 | FedEx Rewards offers | Ad / Promo | Marketing | Open thread
2026-06-15 | WREGIS — bulletin | Newsletter | Registry newsletter | Open thread
2026-06-15 | CJR Renewables — Intersolar (2 more) | Ad / Promo | Event marketing | Open thread
2026-06-14 | HartEnergy — leadership resources | Newsletter | Industry newsletter | Open thread
2026-06-15 | NC Legislation Committee update | Industry | Policy update | Open thread
2026-06-13 | ChatGPT — what's new | Ad / Promo | OpenAI marketing | Open thread