## Alerts
alert_id | site_name | hardware_name | event_type_name | description | severity | is_resolved | is_acknowledged | alert_start | alert_end | resolved_time | timezone | asset_code | impact | capacity | resolved_by
154126617 | Gallia Academy | Elkor Production Meter (Main) | Power Meter Check 2.0 | Current mismatch A = 27.7 Amps, B = 33.6 Amps, C = 33.8 Amps | 0 | TRUE | FALSE | 2026-06-09 13:02 | 2026-06-09 13:47 | 2026-06-09 13:47 | US/Eastern | MTR | 0 | 360 | Unable to verify name
154109089 | Gallia Academy | Elkor Production Meter (Main) | Power Meter Check 2.0 | Current mismatch A = 14.1 Amps, B = 16.8 Amps, C = 17.1 Amps | 0 | TRUE | FALSE | 2026-06-09 10:41 | 2026-06-09 12:51 | 2026-06-09 12:51 | US/Eastern | MTR | 0 | 360 | Unable to verify name
154109092 | Gallia Academy | Elkor Production Meter (Remote) | Power Meter Check 2.0 | Current mismatch A = 12.4 Amps, B = 14.6 Amps, C = 14.9 Amps | 0 | TRUE | FALSE | 2026-06-09 11:19 | 2026-06-09 11:41 | 2026-06-09 11:41 | US/Eastern | MTR | 0 | 360 | Unable to verify name
154117998 | Gallia Academy | Elkor Production Meter (Remote) | Power Meter Check 2.0 | Current mismatch A = 18.8 Amps, B = 21.4 Amps, C = 23.0 Amps | 0 | TRUE | FALSE | 2026-06-09 11:55 | 2026-06-09 12:29 | 2026-06-09 12:29 | US/Eastern | MTR | 0 | 360 | Unable to verify name
154085011 | Rio Grande Elementary | Elkor Production Meter | Power Meter Check 2.0 | Power phase error A = -0.1 kW, B = 0.1 kW, C = -0.1 kW | 0 | TRUE | FALSE | 2026-06-09 01:06 | 2026-06-09 10:32 | 2026-06-09 10:32 | US/Eastern | MTR | 0 | 364 | Unable to verify name
154084266 | RIT |  | Rule Tool Alert | Errors: , Performance (6) Communication: All tests passed | 5 | FALSE | FALSE | 2026-06-09 00:57 |  |  | US/Eastern | UNK | 0
154081162 | Monroe Landfill |  | Rule Tool Alert | Errors: , Performance (51) Communication: 2 test suites failed out of 5 (3 new messages) | 5 | FALSE | FALSE | 2026-06-09 00:22 |  |  | US/Eastern | UNK | 0
154109663 | Monroe Landfill | Solectria PVI 60KTL Inverter - 20 | .Chint / Solectria / Canadian String Inv Faults | Insulation Resistance Low - IsolationErr | 5 | FALSE | FALSE | 2026-06-09 10:30 |  |  | US/Eastern | INV | 100 | 60
154103411 | Warbler | PowerManager 2200 | Gateway heartbeat | This error may be the result of one of the following: 1. Wiring problem between the gateway and the internet connection. | 0 | TRUE | FALSE | 2026-06-09 08:33 | 2026-06-09 09:41 | 2026-06-09 09:41 | US/Eastern | GTW | 0 | 5763 | Unable to verify name
154098245 | Whitetail |  | Rule Tool Alert | Errors: , Performance (4) Communication: 2 test suites failed out of 5 (4 new messages) | 5 | FALSE | FALSE | 2026-06-09 07:09 |  |  | US/Eastern | UNK | 0
154133380 | Whitetail | GameChange Tracker Control 2.1 | Gamechange Tracker Alert | Individual Tracker Alarm60: Tracking Disabled Individual Tracker Alarm60: E-Stop is pressed | 5 | FALSE | FALSE | 2026-06-09 13:56 |  |  | US/Eastern | TKR | 0 | 0
154100624 | Whitetail | GameChange Tracker Control 2.2 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:20 | 2026-06-09 08:22 | 2026-06-09 08:22 | US/Eastern | TKR | 0 | 0 | Unable to verify name
154111607 | Whitetail | GameChange Tracker Control 2.1 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:44 | 2026-06-09 10:46 | 2026-06-09 10:46 | US/Eastern | TKR | 0 | 0 | Unable to verify name
154129153 | Whitetail | GameChange Tracker Control 2.3 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:22 | 2026-06-09 13:24 | 2026-06-09 13:24 | US/Eastern | TKR | 0 | 0 | Unable to verify name
154095361 | Whitetail | GameChange Tracker Control 2.1 | Gamechange Tracker Alert | Individual Tracker Alarm60: Tracking Disabled Individual Tracker Alarm60: E-Stop is pressed | 0 | TRUE | FALSE | 2026-06-09 04:56 | 2026-06-09 07:03 | 2026-06-09 07:03 | US/Eastern | TKR | 0 | 0 | Unable to verify name
154098258 | Whitetail | GameChange Tracker Control 2.1 | Gamechange Tracker Alert | Individual Tracker Alarm60: Tracking Disabled Individual Tracker Alarm60: E-Stop is pressed | 0 | TRUE | FALSE | 2026-06-09 07:06 | 2026-06-09 07:44 | 2026-06-09 07:44 | US/Eastern | TKR | 0 | 0 | Unable to verify name
154099018 | Whitetail | GameChange Tracker Control 2.1 | Gamechange Tracker Alert | Individual Tracker Alarm60: Tracking Disabled Individual Tracker Alarm60: E-Stop is pressed | 0 | TRUE | FALSE | 2026-06-09 07:45 | 2026-06-09 12:38 | 2026-06-09 12:38 | US/Eastern | TKR | 0 | 0 | Unable to verify name
154123955 | Whitetail | GameChange Tracker Control 2.1 | Gamechange Tracker Alert | Individual Tracker Alarm60: Tracking Disabled Individual Tracker Alarm60: E-Stop is pressed | 0 | TRUE | FALSE | 2026-06-09 12:39 | 2026-06-09 13:42 | 2026-06-09 13:42 | US/Eastern | TKR | 0 | 0 | Unable to verify name
154132133 | Whitetail | GameChange Tracker Control 2.1 | Gamechange Tracker Alert | Individual Tracker Alarm60: Tracking Disabled Individual Tracker Alarm60: E-Stop is pressed | 0 | TRUE | FALSE | 2026-06-09 13:46 | 2026-06-09 13:55 | 2026-06-09 13:55 | US/Eastern | TKR | 0 | 0 | Unable to verify name
154097370 | Bulloch 1B | Inverter 23 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 06:20 | 2026-06-09 06:24 | 2026-06-09 06:24 | US/Eastern | INV | 0 | 125 | Unable to verify name
154102665 | Bulloch 1B | Inverter 17 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:58 | 2026-06-09 09:04 | 2026-06-09 09:04 | US/Eastern | INV | 0 | 125 | Unable to verify name
154105994 | Bulloch 1B | Inverter 14 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 09:34 | 2026-06-09 09:38 | 2026-06-09 09:38 | US/Eastern | INV | 0 | 125 | Unable to verify name
154118495 | Bulloch 1B | Inverter 16 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:50 | 2026-06-09 11:52 | 2026-06-09 11:52 | US/Eastern | INV | 0 | 125 | Unable to verify name
154130938 | Bulloch 1B | Inverter 24 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:35 | 2026-06-09 13:37 | 2026-06-09 13:37 | US/Eastern | INV | 0 | 125 | Unable to verify name
154130883 | Bulloch 1B | Inverter 19 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:37 | 2026-06-09 13:38 | 2026-06-09 13:38 | US/Eastern | INV | 0 | 125 | Unable to verify name
154132157 | Bulloch 1B | Inverter 18 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:47 | 2026-06-09 13:48 | 2026-06-09 13:48 | US/Eastern | INV | 0 | 125 | Unable to verify name
154132439 | Bulloch 1B | Inverter 22 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:49 | 2026-06-09 13:54 | 2026-06-09 13:54 | US/Eastern | INV | 0 | 125 | Unable to verify name
154097349 | Bulloch 1B | Inverter 17 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 06:18 | 2026-06-09 06:20 | 2026-06-09 06:20 | US/Eastern | INV | 0 | 125 | Unable to verify name
154100230 | Bulloch 1B | Inverter 22 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:12 | 2026-06-09 08:16 | 2026-06-09 08:16 | US/Eastern | INV | 0 | 125 | Unable to verify name
154107886 | Bulloch 1B | Inverter 18 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:02 | 2026-06-09 10:04 | 2026-06-09 10:04 | US/Eastern | INV | 0 | 125 | Unable to verify name
154124031 | Bulloch 1B | Inverter 19 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:38 | 2026-06-09 12:42 | 2026-06-09 12:42 | US/Eastern | INV | 0 | 125 | Unable to verify name
154084380 | Richmond |  | Rule Tool Alert | Errors: , Performance (2) Communication: 1 test suite failed out of 5 (2 new messages) | 5 | FALSE | FALSE | 2026-06-09 00:59 |  |  | US/Eastern | UNK | 0
154093706 | Upson |  | Rule Tool Alert | Errors: , Performance (1) Communication: All tests passed | 5 | FALSE | FALSE | 2026-06-09 03:51 |  |  | US/Eastern | UNK | 0
154125187 | McLean |  | Rule Tool Alert | Errors: , Performance (2) Communication: 2 test suites failed out of 5 (11 new messages) | 5 | FALSE | FALSE | 2026-06-09 12:52 |  |  | US/Eastern | UNK | 0
154092645 | Shorthorn | TRACKER CONTROL (ST1) | Solar FlexRack Tracker Alert (revG) | Slave Alarms S 54: Emergency stop button pressed Slave Alarms S 48: State Of Charge is under the critical threshold | 5 | FALSE | FALSE | 2026-06-09 03:26 |  |  | US/Eastern | TKR | 0 | 0
154137284 | Shorthorn | TRACKER CONTROL (ST1) | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 5 | FALSE | FALSE | 2026-06-09 14:18 |  |  | US/Eastern | TKR | 0 | 0
154118453 | Shorthorn | METER - PRODUCTION | Power Meter Check 2.0 | Current mismatch A = 16.0 Amps, B = 19.0 Amps, C = 16.3 Amps | 0 | TRUE | FALSE | 2026-06-09 11:48 | 2026-06-09 12:42 | 2026-06-09 12:42 | US/Eastern | MTR | 0 | 9000 | Unable to verify name
154111515 | Shorthorn | METER - PRODUCTION | Power Meter Check 2.0 | Current mismatch A = 9.4 Amps, B = 11.3 Amps, C = 9.4 Amps | 0 | TRUE | FALSE | 2026-06-09 10:44 | 2026-06-09 10:52 | 2026-06-09 10:52 | US/Eastern | MTR | 0 | 9000 | Unable to verify name
154112509 | Shorthorn | METER - PRODUCTION | Power Meter Check 2.0 | Current mismatch A = 12.4 Amps, B = 14.5 Amps, C = 12.7 Amps | 0 | TRUE | FALSE | 2026-06-09 10:56 | 2026-06-09 10:58 | 2026-06-09 10:58 | US/Eastern | MTR | 0 | 9000 | Unable to verify name
154115235 | Shorthorn | METER - PRODUCTION | Power Meter Check 2.0 | Current mismatch A = 13.3 Amps, B = 15.4 Amps, C = 13.3 Amps | 0 | TRUE | FALSE | 2026-06-09 11:20 | 2026-06-09 11:22 | 2026-06-09 11:22 | US/Eastern | MTR | 0 | 9000 | Unable to verify name
154147117 | Washington Solar | INVERTER 6 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 5 | FALSE | FALSE | 2026-06-09 15:35 |  |  | US/Eastern | INV | 0 | 125
154098228 | Washington Solar | INVERTER 18 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 07:06 | 2026-06-09 07:07 | 2026-06-09 07:07 | US/Eastern | INV | 0 | 125 | Unable to verify name
154099577 | Washington Solar | INVERTER 13 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 07:57 | 2026-06-09 07:59 | 2026-06-09 07:59 | US/Eastern | INV | 0 | 125 | Unable to verify name
154101676 | Washington Solar | INVERTER 10 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:40 | 2026-06-09 08:43 | 2026-06-09 08:43 | US/Eastern | INV | 0 | 125 | Unable to verify name
154116900 | Washington Solar | INVERTER 16 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:36 | 2026-06-09 11:37 | 2026-06-09 11:37 | US/Eastern | INV | 0 | 125 | Unable to verify name
154118447 | Washington Solar | INVERTER 4 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:46 | 2026-06-09 11:52 | 2026-06-09 11:52 | US/Eastern | INV | 0 | 125 | Unable to verify name
154119633 | Washington Solar | INVERTER 3 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:56 | 2026-06-09 12:00 | 2026-06-09 12:00 | US/Eastern | INV | 0 | 125 | Unable to verify name
154122876 | Washington Solar | INVERTER 19 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:29 | 2026-06-09 12:31 | 2026-06-09 12:31 | US/Eastern | INV | 0 | 125 | Unable to verify name
154124960 | Washington Solar | INVERTER 17 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:45 | 2026-06-09 12:47 | 2026-06-09 12:47 | US/Eastern | INV | 0 | 125 | Unable to verify name
154130585 | Washington Solar | INVERTER 15 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:33 | 2026-06-09 13:35 | 2026-06-09 13:35 | US/Eastern | INV | 0 | 125 | Unable to verify name
154131661 | Washington Solar | INVERTER 2 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:39 | 2026-06-09 13:41 | 2026-06-09 13:41 | US/Eastern | INV | 0 | 125 | Unable to verify name
154132181 | Washington Solar | INVERTER 7 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:44 | 2026-06-09 13:46 | 2026-06-09 13:46 | US/Eastern | INV | 0 | 125 | Unable to verify name
154132548 | Washington Solar | INVERTER 1 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:47 | 2026-06-09 13:49 | 2026-06-09 13:49 | US/Eastern | INV | 0 | 125 | Unable to verify name
154097271 | Washington Solar | INVERTER 6 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 06:14 | 2026-06-09 06:16 | 2026-06-09 06:16 | US/Eastern | INV | 0 | 125 | Unable to verify name
154097280 | Washington Solar | INVERTER 19 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 06:15 | 2026-06-09 06:17 | 2026-06-09 06:17 | US/Eastern | INV | 0 | 125 | Unable to verify name
154097907 | Washington Solar | INVERTER 13 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 06:50 | 2026-06-09 06:51 | 2026-06-09 06:51 | US/Eastern | INV | 0 | 125 | Unable to verify name
154098557 | Washington Solar | INVERTER 19 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 07:20 | 2026-06-09 07:21 | 2026-06-09 07:21 | US/Eastern | INV | 0 | 125 | Unable to verify name
154099762 | Washington Solar | INVERTER 10 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:04 | 2026-06-09 08:05 | 2026-06-09 08:05 | US/Eastern | INV | 0 | 125 | Unable to verify name
154100262 | Washington Solar | INVERTER 10 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:12 | 2026-06-09 08:15 | 2026-06-09 08:15 | US/Eastern | INV | 0 | 125 | Unable to verify name
154106839 | Washington Solar | INVERTER 15 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 09:47 | 2026-06-09 09:49 | 2026-06-09 09:49 | US/Eastern | INV | 0 | 125 | Unable to verify name
154122245 | Washington Solar | INVERTER 15 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:24 | 2026-06-09 12:25 | 2026-06-09 12:25 | US/Eastern | INV | 0 | 125 | Unable to verify name
154127920 | Harding Solar | ALSOENERGY SMART UPS | Phoenix Contact - Quint UPS Alerts | Battery Over Temperature | 5 | FALSE | FALSE | 2026-06-09 13:10 |  |  | US/Eastern | DA | 0 | 0
154144658 | Whitehall Solar | ALSOENERGY SMART UPS | Phoenix Contact - Quint UPS Alerts | Battery Over Temperature | 5 | FALSE | FALSE | 2026-06-09 15:21 |  |  | US/Eastern | DA | 0 | 0
154098533 | Whitehall Solar | ALSOENERGY SMART UPS | Phoenix Contact - Quint UPS Alerts | Battery Voltage Low | 0 | TRUE | FALSE | 2026-06-09 07:23 | 2026-06-09 07:24 | 2026-06-09 07:24 | US/Eastern | DA | 0 | 0 | Unable to verify name
154097121 | Sunflower Solar | INVERTER 27 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 06:05 | 2026-06-09 06:07 | 2026-06-09 06:07 | US/Eastern | INV | 0 | 125 | Unable to verify name
154098447 | Sunflower Solar | INVERTER 39 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 07:11 | 2026-06-09 07:13 | 2026-06-09 07:13 | US/Eastern | INV | 0 | 125 | Unable to verify name
154098465 | Sunflower Solar | INVERTER 21 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 07:13 | 2026-06-09 07:15 | 2026-06-09 07:15 | US/Eastern | INV | 0 | 125 | Unable to verify name
154101049 | Sunflower Solar | INVERTER 48 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:28 | 2026-06-09 08:29 | 2026-06-09 08:29 | US/Eastern | INV | 0 | 125 | Unable to verify name
154102007 | Sunflower Solar | INVERTER 29 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:48 | 2026-06-09 08:49 | 2026-06-09 08:49 | US/Eastern | INV | 0 | 125 | Unable to verify name
154103840 | Sunflower Solar | INVERTER 76 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 09:04 | 2026-06-09 09:06 | 2026-06-09 09:06 | US/Eastern | INV | 0 | 125 | Unable to verify name
154106539 | Sunflower Solar | INVERTER 68 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 09:41 | 2026-06-09 09:43 | 2026-06-09 09:43 | US/Eastern | INV | 0 | 125 | Unable to verify name
154110758 | Sunflower Solar | INVERTER 62 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:35 | 2026-06-09 10:37 | 2026-06-09 10:37 | US/Eastern | INV | 0 | 125 | Unable to verify name
154111751 | Sunflower Solar | INVERTER 69 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:45 | 2026-06-09 10:46 | 2026-06-09 10:46 | US/Eastern | INV | 0 | 125 | Unable to verify name
154112874 | Sunflower Solar | INVERTER 58 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:56 | 2026-06-09 11:00 | 2026-06-09 11:00 | US/Eastern | INV | 0 | 125 | Unable to verify name
154114871 | Sunflower Solar | INVERTER 47 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:14 | 2026-06-09 11:16 | 2026-06-09 11:16 | US/Eastern | INV | 0 | 125 | Unable to verify name
154116886 | Sunflower Solar | INVERTER 61 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:34 | 2026-06-09 11:35 | 2026-06-09 11:35 | US/Eastern | INV | 0 | 125 | Unable to verify name
154117314 | Sunflower Solar | INVERTER 26 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:35 | 2026-06-09 11:37 | 2026-06-09 11:37 | US/Eastern | INV | 0 | 125 | Unable to verify name
154119357 | Sunflower Solar | INVERTER 73 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:54 | 2026-06-09 11:56 | 2026-06-09 11:56 | US/Eastern | INV | 0 | 125 | Unable to verify name
154122212 | Sunflower Solar | INVERTER 51 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:20 | 2026-06-09 12:22 | 2026-06-09 12:22 | US/Eastern | INV | 0 | 125 | Unable to verify name
154126921 | Sunflower Solar | INVERTER 64 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:03 | 2026-06-09 13:04 | 2026-06-09 13:04 | US/Eastern | INV | 0 | 125 | Unable to verify name
154127811 | Sunflower Solar | INVERTER 23 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:09 | 2026-06-09 13:11 | 2026-06-09 13:11 | US/Eastern | INV | 0 | 125 | Unable to verify name
154132546 | Sunflower Solar | INVERTER 43 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:48 | 2026-06-09 13:50 | 2026-06-09 13:50 | US/Eastern | INV | 0 | 125 | Unable to verify name
154134164 | Sunflower Solar | INVERTER 42 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 14:00 | 2026-06-09 14:02 | 2026-06-09 14:02 | US/Eastern | INV | 0 | 125 | Unable to verify name
154135485 | Sunflower Solar | INVERTER 24 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 14:07 | 2026-06-09 14:09 | 2026-06-09 14:09 | US/Eastern | INV | 0 | 125 | Unable to verify name
154138462 | Sunflower Solar | INVERTER 46 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 14:30 | 2026-06-09 14:31 | 2026-06-09 14:31 | US/Eastern | INV | 0 | 125 | Unable to verify name
154138946 | Sunflower Solar | INVERTER 34 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 14:33 | 2026-06-09 14:34 | 2026-06-09 14:34 | US/Eastern | INV | 0 | 125 | Unable to verify name
154142156 | Sunflower Solar | INVERTER 31 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 14:56 | 2026-06-09 14:57 | 2026-06-09 14:57 | US/Eastern | INV | 0 | 125 | Unable to verify name
154142964 | Sunflower Solar | INVERTER 70 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 15:01 | 2026-06-09 15:03 | 2026-06-09 15:03 | US/Eastern | INV | 0 | 125 | Unable to verify name
154145268 | Sunflower Solar | INVERTER 25 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 15:18 | 2026-06-09 15:23 | 2026-06-09 15:23 | US/Eastern | INV | 0 | 125 | Unable to verify name
154146591 | Sunflower Solar | INVERTER 67 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 15:29 | 2026-06-09 15:31 | 2026-06-09 15:31 | US/Eastern | INV | 0 | 125 | Unable to verify name
154099736 | Sunflower Solar | INVERTER 61 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:01 | 2026-06-09 08:03 | 2026-06-09 08:03 | US/Eastern | INV | 0 | 125 | Unable to verify name
154100945 | Sunflower Solar | INVERTER 73 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 08:24 | 2026-06-09 08:26 | 2026-06-09 08:26 | US/Eastern | INV | 0 | 125 | Unable to verify name
154108672 | Sunflower Solar | INVERTER 23 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:13 | 2026-06-09 10:21 | 2026-06-09 10:21 | US/Eastern | INV | 0 | 125 | Unable to verify name
154109142 | Sunflower Solar | INVERTER 61 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:21 | 2026-06-09 10:23 | 2026-06-09 10:23 | US/Eastern | INV | 0 | 125 | Unable to verify name
154109943 | Sunflower Solar | INVERTER 23 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:29 | 2026-06-09 10:31 | 2026-06-09 10:31 | US/Eastern | INV | 0 | 125 | Unable to verify name
154112990 | Sunflower Solar | INVERTER 46 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 10:57 | 2026-06-09 10:59 | 2026-06-09 10:59 | US/Eastern | INV | 0 | 125 | Unable to verify name
154113343 | Sunflower Solar | INVERTER 26 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:02 | 2026-06-09 11:03 | 2026-06-09 11:03 | US/Eastern | INV | 0 | 125 | Unable to verify name
154114333 | Sunflower Solar | INVERTER 51 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:10 | 2026-06-09 11:12 | 2026-06-09 11:12 | US/Eastern | INV | 0 | 125 | Unable to verify name
154115974 | Sunflower Solar | INVERTER 73 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:27 | 2026-06-09 11:28 | 2026-06-09 11:28 | US/Eastern | INV | 0 | 125 | Unable to verify name
154116026 | Sunflower Solar | INVERTER 61 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:28 | 2026-06-09 11:29 | 2026-06-09 11:29 | US/Eastern | INV | 0 | 125 | Unable to verify name
154116952 | Sunflower Solar | INVERTER 23 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 11:33 | 2026-06-09 11:35 | 2026-06-09 11:35 | US/Eastern | INV | 0 | 125 | Unable to verify name
154123779 | Sunflower Solar | INVERTER 67 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:35 | 2026-06-09 12:37 | 2026-06-09 12:37 | US/Eastern | INV | 0 | 125 | Unable to verify name
154115208 | C & B Graham Energy | INVERTER 8 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 5 | FALSE | FALSE | 2026-06-09 11:21 |  |  | US/Eastern | INV | 100 | 200
154115413 | C & B Graham Energy | INVERTER 10 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 5 | FALSE | FALSE | 2026-06-09 11:21 |  |  | US/Eastern | INV | 100 | 200
154115169 | C & B Graham Energy | INVERTER 14 | Solectria XGI 1000 Series - Fault Alert | Inverter Faults Detected | 5 | FALSE | FALSE | 2026-06-09 11:21 |  |  | US/Eastern | INV | 100 | 200
154115173 | C & B Graham Energy | INVERTER 14 | Solectria XGI 1500 Series - Fault Alert | Hardware self test failure | 5 | FALSE | FALSE | 2026-06-09 11:21 |  |  | US/Eastern | INV | 100 | 200
154140310 | C & B Graham Energy | INVERTER 1 | Solectria XGI 1500 Series - Fault Alert | External Fan Damaged | 5 | FALSE | FALSE | 2026-06-09 14:42 |  |  | US/Eastern | INV | 100 | 200
154144622 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 15:16 | 2026-06-09 15:20 | 2026-06-09 15:20 | US/Eastern | INV | 100 | 200 | Unable to verify name
154115651 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 11:24 | 2026-06-09 11:25 | 2026-06-09 11:25 | US/Eastern | INV | 100 | 200 | Unable to verify name
154117950 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 11:44 | 2026-06-09 11:45 | 2026-06-09 11:45 | US/Eastern | INV | 100 | 200 | Unable to verify name
154118694 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 11:50 | 2026-06-09 11:52 | 2026-06-09 11:52 | US/Eastern | INV | 100 | 200 | Unable to verify name
154121058 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 12:10 | 2026-06-09 12:12 | 2026-06-09 12:12 | US/Eastern | INV | 100 | 200 | Unable to verify name
154121418 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 12:16 | 2026-06-09 12:20 | 2026-06-09 12:20 | US/Eastern | INV | 100 | 200 | Unable to verify name
154122040 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 12:22 | 2026-06-09 12:23 | 2026-06-09 12:23 | US/Eastern | INV | 100 | 200 | Unable to verify name
154122772 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 12:28 | 2026-06-09 12:29 | 2026-06-09 12:29 | US/Eastern | INV | 100 | 200 | Unable to verify name
154123477 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 12:35 | 2026-06-09 12:36 | 2026-06-09 12:36 | US/Eastern | INV | 100 | 200 | Unable to verify name
154124248 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 12:41 | 2026-06-09 12:42 | 2026-06-09 12:42 | US/Eastern | INV | 100 | 200 | Unable to verify name
154126710 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 13:00 | 2026-06-09 13:01 | 2026-06-09 13:01 | US/Eastern | INV | 100 | 200 | Unable to verify name
154127178 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 13:06 | 2026-06-09 13:10 | 2026-06-09 13:10 | US/Eastern | INV | 100 | 200 | Unable to verify name
154127951 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 13:12 | 2026-06-09 13:13 | 2026-06-09 13:13 | US/Eastern | INV | 100 | 200 | Unable to verify name
154129367 | C & B Graham Energy | INVERTER 1 | Solectria XGI 1500 Series - Fault Alert | External Fan Damaged | 0 | TRUE | FALSE | 2026-06-09 13:22 | 2026-06-09 14:02 | 2026-06-09 14:02 | US/Eastern | INV | 100 | 200 | Unable to verify name
154129535 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 13:25 | 2026-06-09 13:26 | 2026-06-09 13:26 | US/Eastern | INV | 100 | 200 | Unable to verify name
154130415 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 13:31 | 2026-06-09 13:32 | 2026-06-09 13:32 | US/Eastern | INV | 100 | 200 | Unable to verify name
154133183 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 13:56 | 2026-06-09 14:00 | 2026-06-09 14:00 | US/Eastern | INV | 100 | 200 | Unable to verify name
154134153 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 14:02 | 2026-06-09 14:04 | 2026-06-09 14:04 | US/Eastern | INV | 100 | 200 | Unable to verify name
154136350 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 14:14 | 2026-06-09 14:24 | 2026-06-09 14:24 | US/Eastern | INV | 100 | 200 | Unable to verify name
154136530 | C & B Graham Energy | INVERTER 1 | Solectria XGI 1500 Series - Fault Alert | External Fan Damaged | 0 | TRUE | FALSE | 2026-06-09 14:16 | 2026-06-09 14:17 | 2026-06-09 14:17 | US/Eastern | INV | 100 | 200 | Unable to verify name
154137954 | C & B Graham Energy | INVERTER 1 | Solectria XGI 1500 Series - Fault Alert | External Fan Damaged | 0 | TRUE | FALSE | 2026-06-09 14:26 | 2026-06-09 14:28 | 2026-06-09 14:28 | US/Eastern | INV | 100 | 200 | Unable to verify name
154138828 | C & B Graham Energy | INVERTER 1 | Solectria XGI 1500 Series - Fault Alert | External Fan Damaged | 0 | TRUE | FALSE | 2026-06-09 14:32 | 2026-06-09 14:36 | 2026-06-09 14:36 | US/Eastern | INV | 100 | 200 | Unable to verify name
154142376 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 14:58 | 2026-06-09 15:02 | 2026-06-09 15:02 | US/Eastern | INV | 100 | 200 | Unable to verify name
154143284 | C & B Graham Energy | INVERTER 4 | Solectria XGI 1500 Series - Fault Alert | Open phase detected | 0 | TRUE | FALSE | 2026-06-09 15:04 | 2026-06-09 15:05 | 2026-06-09 15:05 | US/Eastern | INV | 100 | 200 | Unable to verify name
154096695 | Elk Solar |  | Rule Tool Alert | Errors: , Performance (19) Communication: 3 test suites failed out of 5 (37 new messages) | 5 | FALSE | FALSE | 2026-06-09 05:50 |  |  | US/Eastern | UNK | 0
154094391 | Marble Solar | INVERTER 1 | Sungrow 3150U/3425U/3600U inverter alerts | Stop | 0 | TRUE | FALSE | 2026-06-09 04:19 | 2026-06-09 12:16 | 2026-06-09 12:16 | US/Pacific | INV | 0 | 2875 | Unable to verify name
154100276 | Longleaf Pine Solar, LLC | DIGITAL I/O - XFMR ALARMS | Transformer Monitor | Vacuum fault - Pressure less than -5 psi | 5 | FALSE | FALSE | 2026-06-09 08:13 |  |  | US/Eastern | DA | 0
154122221 | Longleaf Pine Solar, LLC | INVERTER B15 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:23 | 2026-06-09 12:25 | 2026-06-09 12:25 | US/Eastern | INV | 0 | 125 | Unable to verify name
154124855 | Longleaf Pine Solar, LLC | INVERTER B10 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:46 | 2026-06-09 12:47 | 2026-06-09 12:47 | US/Eastern | INV | 0 | 125 | Unable to verify name
154146588 | Longleaf Pine Solar, LLC | INVERTER B18 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 15:29 | 2026-06-09 15:31 | 2026-06-09 15:31 | US/Eastern | INV | 0 | 125 | Unable to verify name
154114262 | Williams Solar, LLC | ALSOENERGY SMART UPS | Phoenix Contact - Quint UPS Alerts (QUINT4 EIP) | Battery Voltage Low | 0 | TRUE | FALSE | 2026-06-09 11:11 | 2026-06-09 11:12 | 2026-06-09 11:12 | US/Eastern | DA | 0 |  | Unable to verify name
154125990 | Williams Solar, LLC | INVERTER B19 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 12:55 | 2026-06-09 12:56 | 2026-06-09 12:56 | US/Eastern | INV | 0 | 125 | Unable to verify name
154128025 | Williams Solar, LLC | INVERTER B7 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:12 | 2026-06-09 13:13 | 2026-06-09 13:13 | US/Eastern | INV | 0 | 125 | Unable to verify name
154128815 | Williams Solar, LLC | INVERTER B10 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:16 | 2026-06-09 13:18 | 2026-06-09 13:18 | US/Eastern | INV | 0 | 125 | Unable to verify name
154134321 | Williams Solar, LLC | INVERTER B15 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 14:00 | 2026-06-09 14:02 | 2026-06-09 14:02 | US/Eastern | INV | 0 | 125 | Unable to verify name
154135141 | Williams Solar, LLC | INVERTER B8 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 14:06 | 2026-06-09 14:07 | 2026-06-09 14:07 | US/Eastern | INV | 0 | 125 | Unable to verify name
154137804 | Williams Solar, LLC | INVERTER B20 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 14:25 | 2026-06-09 14:26 | 2026-06-09 14:26 | US/Eastern | INV | 0 | 125 | Unable to verify name
154146420 | Williams Solar, LLC | INVERTER B13 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 15:26 | 2026-06-09 15:28 | 2026-06-09 15:28 | US/Eastern | INV | 0 | 125 | Unable to verify name
154105758 | Williams Solar, LLC | ALSOENERGY SMART UPS | Phoenix Contact - Quint UPS Alerts (QUINT4 EIP) | Battery Voltage Low | 0 | TRUE | FALSE | 2026-06-09 09:33 | 2026-06-09 09:34 | 2026-06-09 09:34 | US/Eastern | DA | 0 |  | Unable to verify name
154128979 | Williams Solar, LLC | INVERTER B15 | Device communication | This error may be the result of one of the following: 1. Wiring problem between the device and the gateway. | 0 | TRUE | FALSE | 2026-06-09 13:19 | 2026-06-09 13:20 | 2026-06-09 13:20 | US/Eastern | INV | 0 | 125 | Unable to verify name