## Full AI Summaries
Site Key | Site Name | Risk | Generated At | Cached | Full Summary (Plain Text)
S40834 | Green Elementary | 50 | 2026-06-10T00:04 | Yes | All 11 Solectria PVI 28TL inverters, both meters, weather stations, and the gateway are communicating as of Jun 9 at 8:02 PM EDT. Today's production was limited by light rain, with peak hourly output near midday around 200 kWh site-wide. Over the last 30 days, the site averaged an Energy Performance Index of 0.88 with 100% inverter availability. 30-day production reached 92% of estimate. Sampled inverter losses show DC/AC age losses near 5% each and residual loss around 7%, consistent with a maturing system. Meter-to-inverter ratio is 0.97, which is normal. One stale Info-level rule tool alert from Jul 2025 remains open with no production correlation. Forecast calls for rain and light rain Jun 10â12 with highs 82â88Â°F; expect continued weather-limited output.
S40835 | Gallia Academy | 50 | 2026-06-10T00:04 | Yes | Solectria Inverter - 1 has been offline since Apr 6 at 10:57 AM EDT, last upload confirms ~64 days down. Meter-to-inverter ratio today is ~1.06 â consistent with 1 of 20 inverters not producing, confirming an outage rather than comm loss. The remaining 19 inverters are producing today, with site output tracking expected energy under light rain (73Â°F). Inverter 12 shows ~29% residual loss versus peers â a persistent underperformance worth field review. Estimated loss from Inverter - 1: ~12 MWh over 64 days (~5% capacity, ~200 kWh/day per PV model losses for the sampled inverter). 30-day EPI averages 0.92; availability holds at 95%, reflecting the single offline inverter. Meter-to-inverter ratio is 0.97 (30-day) â normal. An active production meter alert flags a current mismatch (A/B/C phases) on the Main Elkor meter as of today â monitoring flag for CT/wiring review. Forecast: rain and light rain through Jun 12, highs 82â88Â°F. Expect reduced output on heavy-rain hours.
S40836 | Rio Grande Elementary | 50 | 2026-06-10T00:04 | Yes | All 13 Solectria 28kW inverters online and producing as of Jun 9 at 8:02 PM EDT, with the site in light rain and near sunset. Recent production tracks reduced expected output under cloudy conditions, with no outages observed. 30-day Energy Performance Index averages 0.88 and inverter availability is 100%. Site produced 53.0 MWh against 58.1 MWh estimate (91%) per the production meter. Sampled-inverter PV model losses show DC/AC age (~5% each) and ~10% residual; no major events identified. Meter-to-inverter ratio is 0.97, normal. Rule tool flags Weather Station 2 (GHI) module temperature stuck at -40Â°F â sensor needs attention but does not affect expected energy (Weather Station 1 drives the model). Forecast calls for light rain and highs of 82â86Â°F through Jun 12; expect continued reduced output under cloud cover.
S44485 | RRH 1 & 2 | 50 | 2026-06-10T00:04 | Yes | All 66 inverters online and producing normally as of Jun 9 at 8:04 PM EDT, with site output tracking expected through the day on production vs. expected. Current conditions are light rain at 70Â°F. 30-day Energy Performance Index averages 1.05, with several days in the 1.11â1.16 range suggesting possible PV model or POA sensor calibration drift worth review. Inverter availability is 100%. Sampled-inverter PV model losses show no notable issues beyond normal age and inverter losses. Meter-to-inverter ratio is 1.00, normal. Two active warnings flag current mismatch on Elkor Production Meters Site 1 and Site 2 (started Jun 9 at 7:41 PM and 7:44 PM); worth monitoring for CT or wiring issue though totals remain consistent with inverters. Forecast is light rain through Jun 12 with highs 73â81Â°F, expect reduced but normal production.
S44566 | RIT | 50 | 2026-06-10T00:05 | Yes | All 27 inverters are online and producing as of Jun 9 at 8:04 PM EDT, with light rain and 72Â°F at site. Today's peak hourly output reached ~1.6 MW around midday, consistent with overcast conditions. The site is healthy. 30-day EPI averages ~1.10, and inverter availability is 94%, pulled down by reduced availability May 27â29 that has since fully recovered. 30-day production totaled 320 MWh vs. 334 MWh estimate (96%). Meter-to-inverter ratio is 0.99, normal. The persistently elevated EPI (~1.10) and large negative residual loss on the sampled inverter suggest a PV model or POA sensor calibration issue worth review, echoed by the rule tool's high energy ratio flags on 19 inverters and low diffuse shade factor configuration warnings. Forecast is light rain with highs 77â82Â°F through Jun 12 â reduced but normal production expected, no equipment risk.
S44882 | Monroe Landfill | 50 | 2026-06-10T00:05 | Yes | Inverter 20 has been offline since May 30, confirmed by an Insulation Resistance Low (IsolationErr) fault and stuck-at-zero AC telemetry. Classified as a forced outage affecting ~73 kW (~3.7% of site capacity), with ~2.3 MWh lost over 11 days (~210 kWh/day expected per the PV model losses for the sampled inverter). All other 26 inverters are online and producing in line with peers as of Jun 9 at 8:03 PM EDT. 30-day EPI averages 1.18 and inverter availability is 96%, the latter dragged by INV-20. Sustained EPI above 1.1 and rule tool high-energy-ratio flags across all inverters suggest a PV model or weather station calibration issue. Meter-to-inverter ratio is 0.99 (normal). Default alerts not set on the Elkor meter. Currently clear, 72Â°F. Light rain forecast Jun 10â11, rain Jun 12; modest production reductions expected.
S51957 | WCPS - William Perry Elementary School | 50 | 2026-06-10T00:05 | Yes | All three CPS SCA60KTL inverters are online and producing as of Jun 9 at 7:38 PM EDT, with the production meter and weather station reporting normally. Today's peak hourly output was modest (~130 kW combined around midday) under variable rain conditions, consistent with the Light rain currently at the site. The site has been underperforming throughout the 30-day window. The Energy Performance Index averages roughly 0.41, with inverter availability at 100% and 30-day production of 29,929 kWh vs. 35,102 kWh estimate (85%). Sampled inverter PV model losses show large DC/AC age losses (~83-88%) and 58% residual loss on Inverter-1, with similar residual losses across all three inverters per the rule tool. This persistent underperformance pattern warrants review. Meter-to-inverter ratio is 1.00 (normal). The Performance Index alert from May 24 reflects this ongoing underperformance. Forecast calls for light rain and warming highs into the low 90s through Jun 12, limiting production.
S51958 | WCPS - Westwood Hills Elementary School | 50 | 2026-06-10T00:05 | Yes | All three inverters are online and producing as of Jun 9 at 6:00 PM EDT, with the production meter at 769.8 kWh today under light rain. Hardware is communicating normally. Current conditions (72Â°F, light rain) are consistent with the reduced afternoon output seen today. No production events occurred in the reporting window. The 30-day Energy Performance Index averaged 0.95 and inverter availability was 100%. Sampled-inverter PV model losses show routine AC/DC age (~3% each) and minor soiling (~1%); no major losses identified. Meter-to-inverter ratio is 1.00, which is normal. The rule tool flagged default-alert configuration items on the Microhard Modem â monitoring-only, no production impact. Forecast calls for light rain and highs of 82â91Â°F through Jun 12; expect continued weather-driven variability with no equipment risk.
S51959 | WCPS - Waynesboro High School | 50 | 2026-06-10T00:05 | Yes | Both inverters are online and producing as of Jun 9 at 7:07 PM EDT, with the site generating 590 kWh today under light rain and overcast conditions. Today's peak hourly output reached ~97 kW around 2:00 PM, consistent with the cloudy weather. Over the last 30 days, the Energy Performance Index averaged 0.84 and inverter availability held at 100%. Production totaled 18.4 MWh, or 90% of the estimate. PV model losses for the sampled inverter show ~4% soiling and a large negative residual, suggesting the PV model may be over-predicting. The meter-to-inverter ratio is 1.00, normal. An informational EPI alert (index 1.32) triggered Jun 9 at 3:21 PM flags a possible weather station calibration issue, consistent with the negative residual losses. Light rain is forecast through Jun 12 with highs reaching 91Â°F, expect continued weather-driven variability.
S51960 | WCPS - Kate Collins Middle School | 50 | 2026-06-10T00:06 | Yes | All 5 CPS SCA60KTL inverters online and producing as of Jun 9 at 6:00 PM EDT under light rain. Today's peak hourly output was ~215 kW around 2:00 PM, consistent with overcast conditions. 30-day Energy Performance Index averages 0.78 with inverter availability at 100%. Production totals 44.5 MWh vs. 56.9 MWh estimated (78%), reflecting frequent rain in the period rather than a discrete event. Inverters 2 and 3 consistently produce ~30â35% less than Inverter 1 across every daylight hour, flagged by the rule tool as low energy ratios (0.67 and 0.62) with excessive residual loss. This is a persistent performance issue worth field investigation (string-level checks, combiner/fuses). Meter-to-inverter ratio is 0.99 (normal). Sampled Inverter 1 model losses show ~10% soiling loss as the main contributor. Forecast is light rain with highs 82â91Â°F through Jun 12; expect continued subdued production.
S54553 | Butler Maple | 50 | 2026-06-10T00:06 | Yes | All hardware is communicating as of Jun 9 around 5:05 PM PDT, and SMA SC4000 Inverter-1 is producing normally, reaching ~3.4 MW midday under light rain conditions. Site is operating normally with no active production events. 30-day Energy Performance Index averages 1.01 and inverter availability is 100%. 30-day production is 1080 MWh, ~116% of estimate. Sampled-inverter PV model losses show typical DC/AC age (~3%) and soiling (~1%); no major losses identified. Tracker losses are negligible (<4 kWh/day). Meter-to-inverter ratio is 0.99, normal. The rule tool flagged a high energy ratio (~1.21) and SEL-351 Relay default alerts not enabled â review sensor calibration and relay alert configuration. Forecast calls for light rain Jun 10, then clear skies Jun 11â12 with highs of 75â79Â°F, favorable for production.
S54613 | Warbler | 50 | 2026-06-10T00:06 | Yes | All 32 Sungrow SG125 inverters are online and communicating as of Jun 9 at 8:06 PM EDT, with all balance-of-plant devices reporting normally. Today's production was limited by cloud cover; recent clear days (Jun 3â5) reached the 4 MW AC cap during midday hours per the production and expected chart. No discrete production events in the last two weeks. Day-to-day variability on May 22â26 and Jun 1â2 aligns with weather, not equipment issues. 30-day Energy Performance Index averaged 0.88 and inverter availability 97%. Sampled-inverter PV model losses show ~8% residual and ~7% combined age-related losses; no major event-driven losses. Meter-to-inverter ratio 0.99, normal. Rule tool clean; no active alerts. Forecast calls for light rain and highs to 99Â°F Jun 10â12; expect reduced output and possible high-temperature derating.
S54681 | Eagle | 50 | 2026-06-10T00:06 | Yes | All 24 CPS SCH125kTL inverters are online and producing in line with peers as of Jun 9 at 8:06 PM EDT, with current output tapering normally near sunset under light rain. Inv-8 shows a persistent ~25% deficit vs. peers (capped near 75 kW during midday hours) visible across recent days in the production chart, coincident with an active External Fan Err fault triggered Jun 9 at 3:42 PM. Classify as partial capability on ~125 kW (~3% of site); ongoing impact ~150 kWh/day. 30-day EPI averages 0.97 with availability at 99%. No major losses identified on the sampled inverter. Meter-to-inverter ratio is 0.99 â normal. Rule tool reports stale comm/weather flags from earlier in the day; hardware table shows all devices uploading within minutes â disregard as stale. Forecast: rain and light rain through Jun 12, highs 79â82Â°F. Expect reduced but normal production.
S59656 | Whitetail | 50 | 2026-06-10T00:07 | Yes | All 80 SunGrow inverters online and reporting as of Jun 9 at 8:06 PM EDT, with the site producing normally through the day under light rain. Current weather is 77Â°F with light rain; peak hourly output reached ~9.4 MW around midday per the production and expected chart. 30-day EPI averages 0.94 and inverter availability 99%. Production-to-estimate ratio is 91%. Sampled-inverter PV model losses show no major losses; tracker lost energy is 0 kWh over 7 days. Meter-to-inverter ratio is 0.99 (normal). Active alerts: a Tracker Control 2.1 E-Stop/Tracking Disabled fault (Jun 9, 7:04 PM) â no tracker energy loss observed; an Aug 2025 comm-loss alert on the original GameChange Tracker Control remains stale. Rule tool flags ~5â6% soiling on inverters 22, 39, 42, and a POA sensor tilt/azimuth misconfiguration worth review. Forecast: light rain with highs 93â99Â°F through Jun 12; expect moderate weather-driven production variability.
S63837 | Bulloch 1B | 50 | 2026-06-10T00:07 | Yes | All 24 inverters online and reporting as of Jun 9 at 8:07 PM EDT, with the site producing 24,000 kWh today against a 24,475 kWh estimate. Current conditions are clear and 82Â°F at sunset, so production is finished for the day. 30-day Energy Performance Index averages 0.99 with inverter availability at 100% over the last 10 days. PV model losses on the sampled inverter show no major issues; tracker lost energy averages ~76 kWh/day, minor. Meter-to-inverter ratio is 0.98, normal. The rule tool flagged three trackers stuck at fixed angles (Position A1 S 22, S 54, S 79) and an average error of 6.2Â° on S 46 â worth field verification but low energy impact. Forecast is clear to light rain with highs reaching 97Â°F by Jun 12; monitor for possible high-temperature derating midweek.
S63838 | Bulloch 1A | 50 | 2026-06-10T00:07 | Yes | All 28 inverters online and reporting fresh telemetry as of Jun 9 at 8:07 PM EDT, with the site past sunset under clear 82Â°F skies. Earlier today the site reached ~3.0 MW around noon, consistent with AC capacity, though afternoon production was variable with passing clouds. Over the last 30 days, the site averaged an EPI of 0.98 and 99.9% inverter availability. Sampled-inverter PV model losses show only minor age and soiling losses; no major losses identified. Meter-to-inverter ratio is 0.98, normal. The rule tool flags Tracker "Position A1 S 16" stuck at 0Â° and AE Smart UPS default alerts not set â monitoring items only. Tracker losses remain small (~24 kWh on Jun 9). Forecast: clear Jun 10, light rain Jun 11, clear Jun 12 with highs reaching 97Â°F â monitor for heat derating.
S63839 | Richmond | 50 | 2026-06-10T00:07 | Yes | All 24 inverters online and producing as of Jun 9 at 8:07 PM EDT, with clear skies and 82Â°F. Current-day production is tracking expected output closely, with a peak around 2.6 MW midday. 30-day Energy Performance Index averages 0.99 and inverter availability is 100% over the last 9 days (site 30-day 99.7%). Sampled-inverter PV model losses show no notable findings; tracker losses are minor (~30â55 kWh/day). Meter-to-inverter ratio is 0.98, normal. The rule tool flags two NCU 1 trackers stuck (Position A1 S 10 at 22.9Â°, A1 S 56 at -21.3Â°) and inverter-group configuration items; impact is limited based on tracker losses. Forecast: clear Jun 10, light rain Jun 11â12 with highs to 99Â°F â some heat derating possible.
S63840 | Upson | 50 | 2026-06-10T00:07 | Yes | All 24 inverters online and reporting as of Jun 9 at 8:07 PM EDT, with the site in post-sunset hours. Recent days have shown variable production consistent with mixed insolation; Jun 8 and Jun 9 ran well below clear-sky days earlier in the week per the production and expected chart. 30-day Energy Performance Index averages 0.96 with inverter availability at 100%. Sampled-inverter PV model losses show no notable items; tracker losses are under 1 kWh/day. Meter-to-inverter ratio is 0.98 over 30 days â normal. The rule tool flags a POA insolation mismatch (+61% vs other sensors) on the Kipp & Zonen SMP-12 POA pyranometer and low BPOA insolation â review sensor calibration/tilt as this can bias EPI. AE Smart UPS default alerts unset; meter PF near zero noted. Forecast is clear with highs 88â93Â°F through Jun 12 â favorable production conditions.
S64602 | McLean | 50 | 2026-06-10T00:08 | Yes | All 40 inverters communicating as of Jun 9 at 8:07 PM EDT, with the most recent uploads within minutes. Site is producing under light rain after a cloudy afternoon; peak output today reached ~4.7 MW around 11 AM. 30-day Energy Performance Index averages 0.93 with no major drops, and inverter availability is 100% in the past week (site 30-day: 99.83%). No notable PV model losses on the sampled inverter; tracker lost energy runs ~50â125 kWh/day, a minor performance drag tied to several stuck/erroring tracker rows. Meter-to-inverter ratio is 0.98, normal. Monitoring flags: PYRANOMETER - BPOA (PY2) offline since Jun 16, 2025 (equipment repair needed); Solar FlexRack tracker slave SOC alarms (S63, S81) since Apr 30; multiple tracker positions reading 0Â° with ~26Â° average error on S10/S63/S81 per the rule tool. Forecast: light rain with highs climbing to 100Â°F by Jun 12 â expect humid, partly clouded production and monitor for heat derating.
S64603 | Shorthorn | 50 | 2026-06-10T00:08 | Yes | All 72 inverters communicating as of Jun 9 at 8:08 PM EDT, with production tapering normally into evening under light rain. Conditions are intermittently cloudy, consistent with reduced midday output today. No production events in the reporting window. A brief site dip on Jun 5 (EPI 0.81, availability 88%) recovered the same day. 30-day EPI averages 0.97 with inverter availability at 99%. Sampled-inverter losses and tracker losses are minor. Meter-to-inverter ratio is 0.98 (normal). Open tracker alerts on ST1 (e-stop, comm loss since Jun 9 at 10:18 AM) and ST2 (low SoC), plus a rule tool flag noting several trackers with elevated position error or stuck at 0Â°. A production meter current mismatch alert (A/B/C phases) triggered Jun 9 at 7:44 PM â worth monitoring for CT/wiring issues. Forecast is light rain with highs 95â100Â°F through Jun 12; expect variable output and possible heat derating.
S65216 | Green Solar | 50 | 2026-06-10T00:08 | Yes | Inverter 1 is online and producing, last reporting at 5:05 PM PDT on Jun 9, with all other hardware communicating normally. Current output is tracking expected energy closely under clear skies and 57Â°F. No production events occurred in the reporting period. Variable output on Jun 3, Jun 5, and Jun 8 reflects intermittent cloud cover, not equipment issues. 30-day Energy Performance Index averaged 0.99 with inverter availability at 99%. Production reached 99% of estimate. No major losses identified in the sampled inverter PV model losses or tracker losses. Meter-to-inverter ratio is 0.99, normal. The rule tool high energy ratio flags reflect partial-day data and are not actionable. Forecast is clear with highs rising to 82Â°F by Jun 12 â favorable production conditions with no derating concerns.
S65784 | Washington Solar | 50 | 2026-06-10T00:08 | No | All 40 inverters communicating as of Jun 9 at 8:08 PM EDT, with site availability at 100% over the last 30 days. Current conditions are light rain at 77Â°F, and today's production reflects a cloudy/rainy profile, peaking near 3.7 MW at 1:00 PM versus ~5 MW expected. The INVERTER 6 invalid-data warning that triggered at 8:03 PM is a brief end-of-day comm blip; Last Update is current. The 30-day Energy Performance Index averages ~1.16, consistently above 1.1, suggesting a PV model or POA sensor calibration issue worth review. 30-day production is 1,246 MWh (94% of estimate). Meter-to-inverter ratio is 0.98 (normal). Rule tool flags stuck VacA/VacB/VacC telemetry across all 40 inverters and many trackers stuck at 0Â° â data-quality flags, not production impacts (tracker losses <3 kWh/day). Forecast: light rain through Jun 10, then hot (97Â°F) Jun 11â12 â monitor for thermal derate.
S65785 | Harding Solar | 50 | 2026-06-10T00:09 | No | All 24 inverters online and producing normally as of Jun 9 at 8:08 PM EDT, with the site tracking expected output closely through the afternoon on the production and expected chart. Clear skies, 77Â°F, light winds. 30-day Energy Performance Index averages 0.96 with inverter availability at 100%. Production totaled 812 MWh vs. 791 MWh estimate (103%). Sampled-inverter PV model losses and tracker losses (~7 kWh/day) are minor. Meter-to-inverter ratio is 0.98, normal. The rule tool flags excessive soiling on Inverters 3, 8, and 17 (~9-11%) and a tracker position error of ~33Â° on TCU 87. An ALSOENERGY Smart UPS Battery Over Temperature alert triggered Jun 9 at 9:14 AM; the UPS continues reporting. Forecast: light rain and highs 90-97Â°F Jun 10-12, which may modestly reduce output.
S65786 | Whitehall Solar | 50 | 2026-06-10T00:09 | No | All 16 inverters online and producing as of Jun 9 at 8:08 PM EDT, with the site reaching ~2,000 kW peak hourly output earlier today per the production and expected chart. Light rain and variable cloud cover suppressed midday output today and on Jun 7â8, consistent with weather. 30-day Energy Performance Index averaged 0.92 and inverter availability averaged 100%. Sampled-inverter PV model losses show no major issues; tracker losses are negligible (~2â5 kWh/day). Meter-to-inverter ratio is 0.98, normal. Rule tool flags TCU 24 stuck at 0Â° and a weather station module-temp sensor reading below ambient â review the back-of-module sensor calibration, as it can affect expected energy. Forecast calls for light rain and highs near 93â100Â°F through Jun 12; high temperatures may cause minor inverter derating but no stow risk with light winds.
S65787 | Sunflower Solar | 50 | 2026-06-10T00:09 | No | All 80 inverters are communicating and operating as of Jun 9 at 8:09 PM EDT, with the production meter, weather station, and trackers reporting normally. Light rain is on site at 79Â°F, with reduced afternoon production today consistent with overcast conditions. No production events in the last two weeks. Daily output has tracked the site performance estimate closely, with full-capacity hours (~9,996 kW) observed Jun 3â5. 30-day EPI averages 0.97 and inverter availability is 99%. No major losses identified on the sampled inverter; tracker losses are minor (~24â50 kWh/day). Meter-to-inverter ratio is 0.98 (normal). A May 17 transformer 90Â°C liquid-temp fault and several rule tool tracker-error and POA insolation-mismatch flags are open with no production correlation; worth review for sensor and tracker alignment. Forecast is light rain with highs 93â99Â°F through Jun 12; expect variable production and some heat-related derate risk.
S65788 | Gray Fox Solar | 50 | 2026-06-10T00:09 | No | All 40 inverters communicating as of Jun 9 at 8:09 PM EDT, with site producing through a light-rain afternoon. Today's peak hourly output reached ~4.9 MW around noon before clouds and rain reduced afternoon output, yielding a partial-day EPI of 0.68. Recent days track expected output closely. No production events in the last two weeks. Jun 8 and Jun 9 both saw weather-driven dips consistent with rain, not equipment issues. 30-day EPI averages 0.88 and inverter availability 97%. Production reached 91% of monthly estimate. Sampled-inverter and tracker losses show nothing notable. Meter-to-inverter ratio is 0.98, normal. One Rule Tool informational alert from Jun 1 has no production correlation. Forecast is light rain to rain Jun 10â12 with highs reaching 100Â°F by Jun 12; expect weather-limited output and possible temperature derating mid-week.
S65918 | C & B Graham Energy | 50 | 2026-06-10T00:09 | No | Site producing through evening with light rain; meter shows 22,830 kWh today across METER 2 and METER 3. Several inverters are confirmed offline based on hourly production: INV-4 (since Jun 9 ~1 PM EDT, forced outage â Shutdown Command), INV-7 and INV-9 (since Jun 2, forced outages), INV-13 (since May 21), INV-17 (since Apr 22), INV-22 (Jun 9 ~5 PM, arc fault), INV-23 (since Apr 10), INV-35 (since Apr 6). INV-14 tripped Jun 9 7:21 AM (hardware self-test) but resumed. Combined ~1.4 MW offline; today's loss ~6â8 MWh vs. ~61 MWh daily estimate. 30-day production totals 740 MWh vs. ~1,782 MWh estimate (42%), reflecting cumulative inverter outages and rainy periods; EPI and availability are uncomputable due to weather station data issues. METER 1 not reporting since Apr 27; meter-to-inverter ratio on reporting meters ~0.79 â low, likely metering data gap. Multiple active fault and comm alerts outstanding, plus pyranometer/weather station offline. Forecast: rain and heavy rain Jun 10â12, reduced production expected.
S66000 | Auburn Solar | 50 | 2026-06-10T00:10 | No | All hardware is communicating as of Jun 9 at 5:09 PM PDT, with Inverter 1 producing normally through the afternoon under light rain conditions. Today's production tracks expected output closely, peaking near 2.0 MW. Over the last 30 days, the site is performing well: EPI averages 1.09 and inverter availability is 100%. Total production of 553 MWh is 123% of estimate. The persistently elevated EPI (>1.1 on several days) suggests a possible PV model or pyranometer calibration drift worth reviewing. Tracker losses are negligible (<13 kWh/day). Meter-to-inverter ratio is 1.01, slightly elevated but consistent over the period â worth monitoring CT/meter configuration. No active alerts and rule tool is clean. Forecast: light rain Jun 10, then clear and warm (75â77Â°F) Jun 11â12, supporting strong production.
S66001 | Sheridan Solar | 50 | 2026-06-10T00:10 | No | Inverter 1 is online and producing, with hardware last update at Jun 9 at 5:09 PM PDT. Current conditions are light rain at 59Â°F, and today's production reached ~2.5 MW at midday under variable irradiance. 30-day Energy Performance Index averages 1.02 and inverter availability is 100%. Total production of 829 MWh is 114% of estimate. No major losses identified on the sampled inverter; tracker losses are minimal (<25 kWh/day). Meter-to-inverter ratio is 0.99 (normal). The rule tool flagged a high energy ratio (1.12) and elevated weather station temperature â worth monitoring for sensor calibration but no production impact. Forecast: light rain Jun 10, clearing Jun 11â12 with highs to 79Â°F. Favorable production conditions ahead.
S66930 | Elk Solar | 50 | 2026-06-10T00:10 | No | Inverter 01.02 has been offline since May 27 at 3:29 AM EDT (forced outage, ~750 kWh/day downtime loss on sampled inverter). Inverter 01.15 also shows zero production with stuck AC telemetry â concurrent outage. Inverters 01.08â01.14 show reduced availability ~30% with ~575â633 kWh/day downtime loss each. Combined ~9 inverter outage represents ~1.1 MW affected capacity, ~5.6 MWh/day loss, ~78 MWh over 14 days. Today's site peak was ~4.3 MW around noon under light rain; weather-limited. 30-day inverter availability 95%; actual/expected 90%. Inverters 01.01 and 01.05 show low energy ratios (0.34, 0.50) â investigate. Production meter reports zero (meter/inverter ratio undefined); voltage calc 173% of meter power â CT/metering issue. NCU 1 and NCU 2 show stuck trackers and abnormal motor currents; tracker losses ~44â73 kWh/day. Forecast: rain through Jun 12, highs 93â100Â°F â expect weather-limited output and possible thermal derating.
S68112 | Wallace Solar | 50 | 2026-06-10T00:10 | No | Inverter 1 is online and producing, with the hardware last reporting at 5:07 PM PDT on Jun 9. Light rain is reducing output today, with a peak hourly output of ~2.4 MWh this morning per the production chart. No production events in the last 30 days. Inverter availability held at 100%. The 30-day EPI averaged 1.07, persistently above 1.0, suggesting a PV model or POA calibration issue rather than a plant problem. Tracker losses were minimal (~0.9â59 kWh/day). Meter-to-inverter ratio is 0.99, normal. The rule tool flags POA insolation +55% higher than other sensors and low BPOA â consistent with the elevated EPI and warrants a pyranometer azimuth/tilt and calibration check. Forecast: light rain Jun 10, then clear and warm Jun 11â12 (75â79Â°F), favorable for production.
S68113 | Marble Solar | 50 | 2026-06-10T00:10 | No | Marble Solar is operating normally as of Jun 9 at 5:09 PM PDT. All hardware is communicating, and Inverter 1 produced about 2.6 MW peak earlier today under clear skies and 61Â°F temperatures. 30-day Energy Performance Index averages 0.99 with inverter availability at 100%. Total production of 758 MWh is 107% of estimate. No major losses identified in the PV model for the sampled inverter; tracker losses are minimal (under 26 kWh/day). Meter-to-inverter ratio is 0.99, within normal range. No active alerts or monitoring flags. Forecast shows light rain Jun 10, then clear and warm (75â77Â°F) Jun 11â12 â favorable production conditions ahead.
S70532 | Longleaf Pine Solar, LLC | 50 | 2026-06-10T00:11 | No | All 40 inverters are online and producing as of Jun 9 at 8:10 PM EDT, with site output tracking irradiance on a light-rain day per the production and expected chart. A site-wide outage occurred Jun 3â4, with zero meter and inverter production both days visible on the production meter chart. Cause is undetermined from available data. Estimated loss ~83 MWh (2 days, 100% capacity, ~42 MWh/day expected). Production fully recovered Jun 5. A similar full-site outage occurred May 17â19, contributing to the EPI dips on those dates. 30-day EPI averages 1.00 excluding outage days; inverter availability is 93%, dragged by the Jun 3â4 event. Meter-to-inverter ratio is 0.98 (normal). Tracker Controller 1 has been offline since Jun 3 with minimal energy impact (~16â30 kWh/day site-wide); TCU 33 shows a 64Â° tracker error per active alerts. Two transformer vacuum-fault alerts remain unacknowledged. Forecast: light rain and highs to 99Â°F through Jun 12; no production risk expected.
S70645 | Williams Solar, LLC | 50 | 2026-06-10T00:11 | No | INVERTER A20 has been offline since Jun 5 with zero production while peers operate normally. The meter-to-inverter ratio of 0.97 confirms a true outage, not a comm loss. A grid overvoltage fault on Jun 8 at 3:10 PM EDT followed by a device communication alert at 3:39 PM points to a forced outage. The other 39 inverters are online and producing normally under clear skies. INVERTER A20 forced outage (Jun 5âpresent, ongoing ~5 days, 125 kW / 2.5% of site capacity). Estimated loss ~5 MWh (5 days Ã ~1 MWh/day expected per PV Model Losses for the sampled inverter). 30-day EPI averages 0.98; inverter availability 99%. Tracker losses minimal (~23 kWh/day). Forecast brings rain and highs near 100Â°F Jun 10â12; possible heat derating and reduced irradiance.
S55935 | Manuel Lawrence Dairy | 50 | 2026-06-10T00:11 | No | Site status cannot be fully assessed â hardware list, production charts, availability, and EPI data are all unavailable for this reporting period. No active alerts are present. Current site time is Jun 9 at 5:11 PM PDT, with clear skies and 91Â°F. Conditions are favorable for production, but actual output cannot be confirmed from available data. The rule tool reports 0% inverter availability and is unable to calculate PV losses across all 15 CPS SCA 60KTL-DO inverters or energy ratio at the Elkor production meter. The IMT reference cell is also reporting invalid module temperature and irradiance, and default alerts are not set on the SFR TDP 2.0 solar tracker. These findings cannot be validated against meter-to-inverter ratio or production charts due to the data retrieval failures noted above. Forecast is clear and hot through Jun 12, with highs reaching 109Â°F. Inverter derating is possible during peak afternoon hours later this week. Data retrieval should be restored to enable proper performance assessment.

## Extracted Facts
site_key | site_name | risk | all_communicating | comm_issues | production_low | production_ok | has_fault | has_alert | weather_sunny | weather_cloudy | weather_rain | inverter_issue | meter_issue | energy_kwh | power_kw | pct_of_expected | temp_f | devices_mentioned
S40834 | Green Elementary | 50 | no | no | no | no | no | YES |  |  | YES | YES |  | 200 |  |  |  | meters; inverters; Meter-to-inverter ratio is 0.97; inverter availability
S40835 | Gallia Academy | 50 | no | YES | no | no | no | YES |  |  | YES | YES |  | 200 |  |  |  | Inverter - 1 has been offline since Apr 6 at 10; inverters are producing today; Meter-to-inverter ratio today is; Inverter - 1
S40836 | Rio Grande Elementary | 50 | no | no | no | YES | no | no |  | YES | YES | YES |  | 28 | 28 |  |  | Weather Station 2; Weather Station 1 drives the model; inverter; Meter-to-inverter ratio is 0.97
S44485 | RRH 1 & 2 | 50 | no | no | no | no | no | YES |  |  | YES | YES | YES |  |  |  |  | inverters online and producing normally as of Jun 9 at 8; Meters Site 1 and Site 2; Inverter availability; inverters. Forecast is light rain through Jun 12 with highs 73â
S44566 | RIT | 50 | no | no | no | no | no | no |  | YES | YES | YES | YES |  |  |  |  | inverters and low diffuse shade factor configuration warnings. Forecast is light rain with highs 77â; inverters are online and producing as of Jun 9 at 8; inverter; Meter-to-inverter ratio is 0.99
S44882 | Monroe Landfill | 50 | no | YES | no | no | YES | YES |  |  | YES | YES | YES | 73 | 73 |  |  | inverters are online and producing in line with peers as of Jun 9 at 8; meter. Currently clear; inverters suggest a PV model or weather station calibration issue. Meter-to-inverter ratio is 0.99; inverter
S51957 | WCPS - William Perry Elementary School | 50 | no | no | YES | no | no | YES |  |  | YES | YES |  | 130 | 130 |  |  | inverter PV model losses; inverters are online and producing as of Jun 9 at 7; meter and weather station reporting normally. Today; inverter availability at 100
S51958 | WCPS - Westwood Hills Elementary School | 50 | no | no | no | no | YES | YES |  |  | YES | YES |  | 769.8 |  |  |  | inverter; inverters are online and producing as of Jun 9 at 6; meter; inverter availability
S51959 | WCPS - Waynesboro High School | 50 | no | no | no | no | no | YES |  | YES | YES | YES | YES | 590 | 97 |  |  | inverters are online and producing as of Jun 9 at 7; weather station calibration issue; inverter availability; inverter show
S51960 | WCPS - Kate Collins Middle School | 50 | no | no | no | no | no | no |  | YES | YES | YES | YES | 215 | 215 |  |  | inverters online and producing as of Jun 9 at 6; Inverter 1 across every daylight hour; Inverter 1; inverter availability at 100
S54553 | Butler Maple | 50 | YES | no | no | no | YES | YES | YES |  | YES | YES |  | 4 |  |  |  | inverter PV model losses; Inverter-1 is producing normally; Tracker losses; Meter-to-inverter ratio is 0.99
S54613 | Warbler | 50 | no | no | no | no | no | no |  | YES | YES | YES | YES |  |  |  |  | inverters are online and communicating as of Jun 9 at 8; Meter-to-inverter ratio 0.99; inverter availability; inverter
S54681 | Eagle | 50 | no | no | no | no | YES | YES |  |  | YES | YES |  | 75 | 75 |  |  | inverters are online and producing in line with peers as of Jun 9 at 8; inverter. Meter-to-inverter ratio is 0.99 â
S59656 | Whitetail | 50 | no | no | no | no | YES | YES |  |  | YES | YES |  | 0 |  |  |  | tracker lost energy is 0 kWh over 7 days. Meter-to-inverter ratio is 0.99; inverters 22; tracker energy loss observed; Tracker Control remains stale.
S63837 | Bulloch 1B | 50 | no | no | no | no | no | no |  |  | YES | YES | YES | 24000 |  |  |  | trackers stuck at fixed angles; inverter availability at 100; inverters online and reporting as of Jun 9 at 8; Meter-to-inverter ratio is 0.98
S63838 | Bulloch 1A | 50 | no | no | no | no | YES | YES |  |  | YES | YES |  | 24 |  |  |  | inverters online and reporting fresh telemetry as of Jun 9 at 8; Tracker losses remain small; Tracker; inverter
S63839 | Richmond | 50 | no | no | no | YES | no | no | YES |  | YES | YES |  | 55 |  |  |  | inverter PV model losses show no notable findings; inverter-group configuration items; trackers stuck; inverter availability
S63840 | Upson | 50 | no | no | no | no | YES | YES |  |  |  | YES |  | 1 |  |  |  | meter PF near zero noted. Forecast is clear with highs 88â; tracker losses are under 1 kWh; inverter availability at 100; inverter
S64602 | McLean | 50 | no | YES | no | no | no | YES |  | YES | YES | YES | YES | 125 |  |  |  | PYRANOMETER - BPOA; tracker positions reading 0Â; tracker slave SOC alarms; tracker rows. Meter-to-inverter ratio is 0.98
S64603 | Shorthorn | 50 | no | YES | no | no | no | YES |  | YES | YES | YES | YES |  |  |  |  | inverter availability at 99; inverters communicating as of Jun 9 at 8; trackers with elevated position error or stuck at 0Â; tracker alerts
S65216 | Green Solar | 50 | no | YES | no | no | no | no | YES | YES |  | YES | YES |  |  |  |  | inverter availability at 99; tracker losses. Meter-to-inverter ratio is 0.99; inverter; Inverter 1 is online and producing
S65784 | Washington Solar | 50 | no | no | no | no | no | no |  | YES | YES | YES | YES | 3 |  |  |  | inverters and many trackers stuck at 0Â; inverters communicating as of Jun 9 at 8; INVERTER 6 invalid-data warning that triggered at 8; Meter-to-inverter ratio is 0.98
S65785 | Harding Solar | 50 | no | no | no | no | no | YES | YES |  | YES | YES | YES | 7 |  |  |  | inverters online and producing normally as of Jun 9 at 8; tracker position error of; inverter; Inverters 3
S65786 | Whitehall Solar | 50 | no | no | no | no | no | no |  | YES | YES | YES | YES | 2000 | 2000 |  |  | inverter derating but no stow risk with light winds.; weather station module-temp sensor reading below ambient â; inverter; tracker losses are negligible
S65787 | Sunflower Solar | 50 | no | no | no | no | YES | no |  | YES | YES | YES | YES | 9996 | 9996 |  |  | inverters are communicating and operating as of Jun 9 at 8; tracker alignment. Forecast is light rain with highs 93â; tracker-error and POA insolation-mismatch flags; inverter
S65788 | Gray Fox Solar | 50 | no | no | no | no | no | YES |  |  | YES | YES | YES |  |  |  |  | inverter and tracker losses show nothing notable. Meter-to-inverter ratio is 0.98; inverter availability 97; inverters communicating as of Jun 9 at 8
S65918 | C & B Graham Energy | 50 | no | YES | no | no | YES | YES |  |  | YES | YES | YES | 22830 |  |  |  | meter shows 22; inverters are confirmed offline based on; meter-to-inverter ratio on reporting meters; metering data gap. Multiple
S66000 | Auburn Solar | 50 | YES | no | no | no | no | no |  |  | YES | YES |  | 13 |  |  |  | Inverter 1 producing normally through the afternoon under light rain conditions. Today; Tracker losses; meter configuration. No active alerts and rule tool is clean. Forecast; pyranometer calibration drift worth reviewing.
S66001 | Sheridan Solar | 50 | no | no | no | no | no | no |  |  | YES | YES |  | 25 |  |  |  | tracker losses are minimal; weather station temperature â; inverter; Meter-to-inverter ratio is 0.99
S66930 | Elk Solar | 50 | no | YES | no | no | no | no |  |  | YES | YES | YES | 750 |  |  |  | trackers and abnormal motor currents; Inverter 01.02 has been offline since May 27 at 3; inverter outage represents; inverter ratio undefined
S68112 | Wallace Solar | 50 | no | no | no | no | no | YES |  |  | YES | YES | YES | 59 |  |  |  | Tracker losses were minimal; pyranometer azimuth; Inverter availability; Meter-to-inverter ratio is 0.99
S68113 | Marble Solar | 50 | YES | no | no | no | no | no | YES |  | YES | YES |  | 26 |  |  |  | inverter availability at 100; inverter; Meter-to-inverter ratio is 0.99; tracker losses
S70532 | Longleaf Pine Solar, LLC | 50 | no | YES | no | no | YES | YES |  |  | YES | YES | YES | 30 |  |  |  | tracker error per; Tracker Controller 1 has been offline since Jun 3 with minimal energy impact; inverters are online and producing as of Jun 9 at 8; meter and inverter production both days visible on the
S70645 | Williams Solar, LLC | 50 | no | YES | no | no | YES | YES | YES |  | YES | YES |  | 125 | 125 |  |  | INVERTER A20 has been offline since Jun 5 with zero production while peers operate normally. The; meter-to-inverter ratio; Tracker losses minimal; inverter
S55935 | Manuel Lawrence Dairy | 50 | no | no | no | no | YES | no | YES |  |  | YES | YES |  |  |  |  | Inverter derating is possible during peak afternoon hours later this week. Data retrieval should be restored to enable proper performance assessment.; inverter availability and is unable to calculate PV losses across all 15 CPS SCA 60KTL-DO inverters or energy ratio at the Elkor production meter. The IMT reference cell is also reporting invalid module temperature and irradiance; tracker. These findings cannot be validated against meter-to-inverter ratio or production charts due to the data retrieval failures noted above. Forecast is clear and hot through Jun 12

## Site Rankings
Rank | Site Key | Site Name | Risk Score | Comm OK | Prod OK | Has Fault | Has Alert | Weather
1 | S40834 | Green Elementary | 50 | ? | ? |  | YES | Rainy
2 | S40835 | Gallia Academy | 50 | ISSUE | ? |  | YES | Rainy
3 | S40836 | Rio Grande Elementary | 50 | ? | OK |  |  | Rainy
4 | S44485 | RRH 1 & 2 | 50 | ? | ? |  | YES | Rainy
5 | S44566 | RIT | 50 | ? | ? |  |  | Rainy
6 | S44882 | Monroe Landfill | 50 | ISSUE | ? | YES | YES | Rainy
7 | S51957 | WCPS - William Perry Elementary School | 50 | ? | LOW |  | YES | Rainy
8 | S51958 | WCPS - Westwood Hills Elementary School | 50 | ? | ? | YES | YES | Rainy
9 | S51959 | WCPS - Waynesboro High School | 50 | ? | ? |  | YES | Rainy
10 | S51960 | WCPS - Kate Collins Middle School | 50 | ? | ? |  |  | Rainy
11 | S54553 | Butler Maple | 50 | OK | ? | YES | YES | Rainy
12 | S54613 | Warbler | 50 | ? | ? |  |  | Rainy
13 | S54681 | Eagle | 50 | ? | ? | YES | YES | Rainy
14 | S59656 | Whitetail | 50 | ? | ? | YES | YES | Rainy
15 | S63837 | Bulloch 1B | 50 | ? | ? |  |  | Rainy
16 | S63838 | Bulloch 1A | 50 | ? | ? | YES | YES | Rainy
17 | S63839 | Richmond | 50 | ? | OK |  |  | Rainy
18 | S63840 | Upson | 50 | ? | ? | YES | YES
19 | S64602 | McLean | 50 | ISSUE | ? |  | YES | Rainy
20 | S64603 | Shorthorn | 50 | ISSUE | ? |  | YES | Rainy
21 | S65216 | Green Solar | 50 | ISSUE | ? |  |  | Cloudy
22 | S65784 | Washington Solar | 50 | ? | ? |  |  | Rainy
23 | S65785 | Harding Solar | 50 | ? | ? |  | YES | Rainy
24 | S65786 | Whitehall Solar | 50 | ? | ? |  |  | Rainy
25 | S65787 | Sunflower Solar | 50 | ? | ? | YES |  | Rainy
26 | S65788 | Gray Fox Solar | 50 | ? | ? |  | YES | Rainy
27 | S65918 | C & B Graham Energy | 50 | ISSUE | ? | YES | YES | Rainy
28 | S66000 | Auburn Solar | 50 | OK | ? |  |  | Rainy
29 | S66001 | Sheridan Solar | 50 | ? | ? |  |  | Rainy
30 | S66930 | Elk Solar | 50 | ISSUE | ? |  |  | Rainy
31 | S68112 | Wallace Solar | 50 | ? | ? |  | YES | Rainy
32 | S68113 | Marble Solar | 50 | OK | ? |  |  | Rainy
33 | S70532 | Longleaf Pine Solar, LLC | 50 | ISSUE | ? | YES | YES | Rainy
34 | S70645 | Williams Solar, LLC | 50 | ISSUE | ? | YES | YES | Rainy
35 | S55935 | Manuel Lawrence Dairy | 50 | ? | ? | YES |  | Sunny