## Site Analysis
site_key | site_name | comm_status | prod_status | has_active_alert | weather_impact | urgency_score | urgency_label | production_kwh | power_kw | pct_expected | perf_index | temp_f | pct_loss | device_count | devices_mentioned | action_count | embedded_url_count | summary_length | plain_text
S40834 | Green Elementary | Unknown | Unknown | Yes | Yes | 3 | High | 200 | [5 empty] | 7 | meters; Meter-to-inverter ratio is 0.97; gateway are communicating as of Jun 9 at 8; weather stations; inverter losses | 0 | 3 | 1216 | All 11 Solectria PVI 28TL inverters, both meters, weather stations, and the gateway are communicating as of Jun 9 at 8:02 PM EDT. Today's production was limited by light rain, with peak hourly output near midday around 200 kWh site-wide. Over the last 30 days, the site averaged an Energy Performance Index of 0.88 with 100% inverter availability. 30-day production reached 92% of estimate. Sampled inverter losses show DC/AC age losses near 5% each and residual loss around 7%, consistent with a m
S40835 | Gallia Academy | Partial / Issues | Below Expected | Yes | Yes | 3 | High | 200 | [5 empty] | 10 | meter alert; meter as of today â; Inverter 12 shows; inverters are producing today; inverters not producing | 0 | 5 | 1647 | Solectria Inverter - 1 has been offline since Apr 6 at 10:57 AM EDT, last upload confirms ~64 days down. Meter-to-inverter ratio today is ~1.06 â consistent with 1 of 20 inverters not producing, confirming an outage rather than comm loss. The remaining 19 inverters are producing today, with site output tracking expected energy under light rain (73Â°F). Inverter 12 shows ~29% residual loss versus peers â a persistent underperformance worth field review. Estimated loss from Inverter - 1: ~12
S40836 | Rio Grande Elementary | Unknown | Below Expected | No | Yes | 2 | Medium | 28 | 28 |  |  |  |  | 8 | Weather Station 2; Meter-to-inverter ratio is 0.97; meter; inverters online and producing as of Jun 9 at 8; sensor needs attention but does not affect expected energy | 1 | 5 | 1485 | All 13 Solectria 28kW inverters online and producing as of Jun 9 at 8:02 PM EDT, with the site in light rain and near sunset. Recent production tracks reduced expected output under cloudy conditions, with no outages observed. 30-day Energy Performance Index averages 0.88 and inverter availability is 100%. Site produced 53.0 MWh against 58.1 MWh estimate (91%) per the production meter. Sampled-inverter PV model losses show DC/AC age (~5% each) and ~10% residual; no major events identified. Mete
S44485 | RRH 1 & 2 | Unknown | Unknown | Yes | Yes | 2 | Medium | [6 empty] | 6 | inverter PV model losses show no notable issues beyond normal age and inverter losses. Meter-to-inverter ratio is 1.00; sensor calibration drift worth review.; inverters. Forecast is light rain through Jun 12 with highs 73â; inverters online and producing normally as of Jun 9 at 8; Inverter availability | 0 | 4 | 1346 | All 66 inverters online and producing normally as of Jun 9 at 8:04 PM EDT, with site output tracking expected through the day on production vs. expected. Current conditions are light rain at 70Â°F. 30-day Energy Performance Index averages 1.05, with several days in the 1.11â1.16 range suggesting possible PV model or POA sensor calibration drift worth review. Inverter availability is 100%. Sampled-inverter PV model losses show no notable issues beyond normal age and inverter losses. Meter-to
S44566 | RIT | Unknown | Unknown | No | Yes | 3 | High | [6 empty] | 6 | Meter-to-inverter ratio is 0.99; sensor calibration issue worth review; inverters are online and producing as of Jun 9 at 8; inverter; inverters and low diffuse shade factor configuration warnings. Forecast is light rain with highs 77â | 0 | 5 | 1520 | All 27 inverters are online and producing as of Jun 9 at 8:04 PM EDT, with light rain and 72Â°F at site. Today's peak hourly output reached ~1.6 MW around midday, consistent with overcast conditions. The site is healthy. 30-day EPI averages ~1.10, and inverter availability is 94%, pulled down by reduced availability May 27â29 that has since fully recovered. 30-day production totaled 320 MWh vs. 334 MWh estimate (96%). Meter-to-inverter ratio is 0.99, normal. The persistently elevated EPI (~1
S44882 | Monroe Landfill | Partial / Issues | Unknown | Yes | Yes | 3 | High | 73 | 73 |  |  |  |  | 6 | inverters suggest a PV model or weather station calibration issue. Meter-to-inverter ratio is 0.99; inverters are online and producing in line with peers as of Jun 9 at 8; inverter availability is 96; inverter; Inverter 20 has been offline since May 30 | 0 | 5 | 1409 | Inverter 20 has been offline since May 30, confirmed by an Insulation Resistance Low (IsolationErr) fault and stuck-at-zero AC telemetry. Classified as a forced outage affecting ~73 kW (~3.7% of site capacity), with ~2.3 MWh lost over 11 days (~210 kWh/day expected per the PV model losses for the sampled inverter). All other 26 inverters are online and producing in line with peers as of Jun 9 at 8:03 PM EDT. 30-day EPI averages 1.18 and inverter availability is 96%, the latter dragged by INV-20
S51957 | WCPS - William Perry Elementary School | Unknown | Below Expected | Yes | Yes | 2 | Medium | 130 | 130 |  |  |  |  | 7 | inverters are online and producing as of Jun 9 at 7; inverters per the; Meter-to-inverter ratio is 1.00; inverter availability at 100; Inverter-1 | 0 | 5 | 1568 | All three CPS SCA60KTL inverters are online and producing as of Jun 9 at 7:38 PM EDT, with the production meter and weather station reporting normally. Today's peak hourly output was modest (~130 kW combined around midday) under variable rain conditions, consistent with the Light rain currently at the site. The site has been underperforming throughout the 30-day window. The Energy Performance Index averages roughly 0.41, with inverter availability at 100% and 30-day production of 29,929 kWh vs
S51958 | WCPS - Westwood Hills Elementary School | All Communicating | Unknown | Yes | Yes | 3 | High | 769.8 | [5 empty] | 6 | meter; inverters are online and producing as of Jun 9 at 6; Meter-to-inverter ratio is 1.00; inverter; inverter availability | 0 | 5 | 1498 | All three inverters are online and producing as of Jun 9 at 6:00 PM EDT, with the production meter at 769.8 kWh today under light rain. Hardware is communicating normally. Current conditions (72Â°F, light rain) are consistent with the reduced afternoon output seen today. No production events occurred in the reporting window. The 30-day Energy Performance Index averaged 0.95 and inverter availability was 100%. Sampled-inverter PV model losses show routine AC/DC age (~3% each) and minor soiling
S51959 | WCPS - Waynesboro High School | Unknown | Unknown | Yes | Yes | 2 | Medium | 590 | 97 |  |  |  |  | 5 | inverters are online and producing as of Jun 9 at 7; inverter show; weather station calibration issue; meter-to-inverter ratio is 1.00; inverter availability | 0 | 4 | 1366 | Both inverters are online and producing as of Jun 9 at 7:07 PM EDT, with the site generating 590 kWh today under light rain and overcast conditions. Today's peak hourly output reached ~97 kW around 2:00 PM, consistent with the cloudy weather. Over the last 30 days, the Energy Performance Index averaged 0.84 and inverter availability held at 100%. Production totaled 18.4 MWh, or 90% of the estimate. PV model losses for the sampled inverter show ~4% soiling and a large negative residual, suggesti
S51960 | WCPS - Kate Collins Middle School | Unknown | Below Expected | No | Yes | 2 | Medium | 215 | 215 |  |  |  | 35 | 7 | Meter-to-inverter ratio is 0.99; inverters online and producing as of Jun 9 at 6; Inverter 1 across every daylight hour; inverter availability at 100; Inverters 2 and 3 consistently produce | 1 | 5 | 1563 | All 5 CPS SCA60KTL inverters online and producing as of Jun 9 at 6:00 PM EDT under light rain. Today's peak hourly output was ~215 kW around 2:00 PM, consistent with overcast conditions. 30-day Energy Performance Index averages 0.78 with inverter availability at 100%. Production totals 44.5 MWh vs. 56.9 MWh estimated (78%), reflecting frequent rain in the period rather than a discrete event. Inverters 2 and 3 consistently produce ~30â35% less than Inverter 1 across every daylight hour, flagg
S54553 | Butler Maple | All Communicating | Unknown | Yes | Yes | 3 | High | 4 | [5 empty] | 7 | Meter-to-inverter ratio is 0.99; Relay default alerts not enabled â; Tracker losses; inverter PV model losses; sensor calibration and relay alert configuration. Forecast calls for light rain Jun 10 | 0 | 6 | 1714 | All hardware is communicating as of Jun 9 around 5:05 PM PDT, and SMA SC4000 Inverter-1 is producing normally, reaching ~3.4 MW midday under light rain conditions. Site is operating normally with no active production events. 30-day Energy Performance Index averages 1.01 and inverter availability is 100%. 30-day production is 1080 MWh, ~116% of estimate. Sampled-inverter PV model losses show typical DC/AC age (~3%) and soiling (~1%); no major losses identified. Tracker losses are negligible (<
S54613 | Warbler | Unknown | Below Expected | Yes | Yes | 2 | Medium | [6 empty] | 4 | inverter availability; inverters are online and communicating as of Jun 9 at 8; Meter-to-inverter ratio 0.99; inverter | 0 | 5 | 1493 | All 32 Sungrow SG125 inverters are online and communicating as of Jun 9 at 8:06 PM EDT, with all balance-of-plant devices reporting normally. Today's production was limited by cloud cover; recent clear days (Jun 3â5) reached the 4 MW AC cap during midday hours per the production and expected chart. No discrete production events in the last two weeks. Day-to-day variability on May 22â26 and Jun 1â2 aligns with weather, not equipment issues. 30-day Energy Performance Index averaged 0.88 an
S54681 | Eagle | Unknown | Unknown | Yes | Yes | 3 | High | 75 | 75 |  |  |  |  | 2 | inverters are online and producing in line with peers as of Jun 9 at 8; inverter. Meter-to-inverter ratio is 0.99 â | 0 | 5 | 1442 | All 24 CPS SCH125kTL inverters are online and producing in line with peers as of Jun 9 at 8:06 PM EDT, with current output tapering normally near sunset under light rain. Inv-8 shows a persistent ~25% deficit vs. peers (capped near 75 kW during midday hours) visible across recent days in the production chart, coincident with an active External Fan Err fault triggered Jun 9 at 3:42 PM. Classify as partial capability on ~125 kW (~3% of site); ongoing impact ~150 kWh/day. 30-day EPI averages 0.97
S59656 | Whitetail | Unknown | Unknown | Yes | Yes | 3 | High | 0 | [5 empty] | 9 | tracker energy loss observed; Tracker Control 2.1 E-Stop; Tracker Control remains stale.; tracker lost energy is 0 kWh over 7 days. Meter-to-inverter ratio is 0.99; inverters online and reporting as of Jun 9 at 8 | 0 | 6 | 1660 | All 80 SunGrow inverters online and reporting as of Jun 9 at 8:06 PM EDT, with the site producing normally through the day under light rain. Current weather is 77Â°F with light rain; peak hourly output reached ~9.4 MW around midday per the production and expected chart. 30-day EPI averages 0.94 and inverter availability 99%. Production-to-estimate ratio is 91%. Sampled-inverter PV model losses show no major losses; tracker lost energy is 0 kWh over 7 days. Meter-to-inverter ratio is 0.99 (norm
S63837 | Bulloch 1B | Unknown | Unknown | Yes | Yes | 2 | Medium | 24000 | [5 empty] | 6 | inverter show no major issues; inverter availability at 100; inverters online and reporting as of Jun 9 at 8; Meter-to-inverter ratio is 0.98; tracker lost energy | 0 | 5 | 1437 | All 24 inverters online and reporting as of Jun 9 at 8:07 PM EDT, with the site producing 24,000 kWh today against a 24,475 kWh estimate. Current conditions are clear and 82Â°F at sunset, so production is finished for the day. 30-day Energy Performance Index averages 0.99 with inverter availability at 100% over the last 10 days. PV model losses on the sampled inverter show no major issues; tracker lost energy averages ~76 kWh/day, minor. Meter-to-inverter ratio is 0.98, normal. The rule tool
S63838 | Bulloch 1A | Unknown | Unknown | Yes | Yes | 3 | High | 24 | [5 empty] | 7 | inverters online and reporting fresh telemetry as of Jun 9 at 8; Tracker losses remain small; UPS default alerts not set â; inverter; Tracker | 0 | 5 | 1445 | All 28 inverters online and reporting fresh telemetry as of Jun 9 at 8:07 PM EDT, with the site past sunset under clear 82Â°F skies. Earlier today the site reached ~3.0 MW around noon, consistent with AC capacity, though afternoon production was variable with passing clouds. Over the last 30 days, the site averaged an EPI of 0.98 and 99.9% inverter availability. Sampled-inverter PV model losses show only minor age and soiling losses; no major losses identified. Meter-to-inverter ratio is 0.98,
S63839 | Richmond | Unknown | On Track | No | Yes | 1 | Low | 55 | [5 empty] | 8 | trackers stuck; tracker losses; inverters online and producing as of Jun 9 at 8; Meter-to-inverter ratio is 0.98; inverter PV model losses show no notable findings | 0 | 5 | 1467 | All 24 inverters online and producing as of Jun 9 at 8:07 PM EDT, with clear skies and 82Â°F. Current-day production is tracking expected output closely, with a peak around 2.6 MW midday. 30-day Energy Performance Index averages 0.99 and inverter availability is 100% over the last 9 days (site 30-day 99.7%). Sampled-inverter PV model losses show no notable findings; tracker losses are minor (~30â55 kWh/day). Meter-to-inverter ratio is 0.98, normal. The rule tool flags two NCU 1 trackers stuc
S63840 | Upson | Unknown | Unknown | Yes | No | 3 | High | 1 | [5 empty] | 10 | sensor calibration; sensors; UPS default alerts unset; Meter-to-inverter ratio is 0.98 over 30 days â; pyranometer and low BPOA insolation â | 0 | 5 | 1512 | All 24 inverters online and reporting as of Jun 9 at 8:07 PM EDT, with the site in post-sunset hours. Recent days have shown variable production consistent with mixed insolation; Jun 8 and Jun 9 ran well below clear-sky days earlier in the week per the production and expected chart. 30-day Energy Performance Index averages 0.96 with inverter availability at 100%. Sampled-inverter PV model losses show no notable items; tracker losses are under 1 kWh/day. Meter-to-inverter ratio is 0.98 over 30
S64602 | McLean | Partial / Issues | Unknown | Yes | Yes | 3 | High | 125 | [5 empty] | 8 | inverters communicating as of Jun 9 at 8; tracker positions reading 0Â; tracker slave SOC alarms; tracker rows. Meter-to-inverter ratio is 0.98; inverter | 1 | 5 | 1523 | All 40 inverters communicating as of Jun 9 at 8:07 PM EDT, with the most recent uploads within minutes. Site is producing under light rain after a cloudy afternoon; peak output today reached ~4.7 MW around 11 AM. 30-day Energy Performance Index averages 0.93 with no major drops, and inverter availability is 100% in the past week (site 30-day: 99.83%). No notable PV model losses on the sampled inverter; tracker lost energy runs ~50â125 kWh/day, a minor performance drag tied to several stuck/er
S64603 | Shorthorn | Partial / Issues | Unknown | Yes | Yes | 3 | High | [6 empty] | 8 | trackers with elevated position error or stuck at 0Â; inverters communicating as of Jun 9 at 8; tracker losses; meter current mismatch alert; inverter losses and | 0 | 7 | 1764 | All 72 inverters communicating as of Jun 9 at 8:08 PM EDT, with production tapering normally into evening under light rain. Conditions are intermittently cloudy, consistent with reduced midday output today. No production events in the reporting window. A brief site dip on Jun 5 (EPI 0.81, availability 88%) recovered the same day. 30-day EPI averages 0.97 with inverter availability at 99%. Sampled-inverter losses and tracker losses are minor. Meter-to-inverter ratio is 0.98 (normal). Open trac
S65216 | Green Solar | Partial / Issues | Unknown | No | Yes | 3 | High | [6 empty] | 4 | inverter availability at 99; tracker losses. Meter-to-inverter ratio is 0.99; Inverter 1 is online and producing; inverter | 0 | 5 | 1459 | Inverter 1 is online and producing, last reporting at 5:05 PM PDT on Jun 9, with all other hardware communicating normally. Current output is tracking expected energy closely under clear skies and 57Â°F. No production events occurred in the reporting period. Variable output on Jun 3, Jun 5, and Jun 8 reflects intermittent cloud cover, not equipment issues. 30-day Energy Performance Index averaged 0.99 with inverter availability at 99%. Production reached 99% of estimate. No major losses identi
S65784 | Washington Solar | Unknown | Unknown | No | Yes | 2 | Medium | 3 | [5 empty] | 6 | inverters communicating as of Jun 9 at 8; tracker losses; inverters and many trackers stuck at 0Â; INVERTER 6 invalid-data warning that triggered at 8; Meter-to-inverter ratio is 0.98 | 0 | 5 | 1542 | All 40 inverters communicating as of Jun 9 at 8:08 PM EDT, with site availability at 100% over the last 30 days. Current conditions are light rain at 77Â°F, and today's production reflects a cloudy/rainy profile, peaking near 3.7 MW at 1:00 PM versus ~5 MW expected. The INVERTER 6 invalid-data warning that triggered at 8:03 PM is a brief end-of-day comm blip; Last Update is current. The 30-day Energy Performance Index averages ~1.16, consistently above 1.1, suggesting a PV model or POA sensor
S65785 | Harding Solar | Unknown | Unknown | Yes | Yes | 2 | Medium | 7 | [5 empty] | 9 | UPS Battery Over Temperature alert; tracker losses; Inverters 3; UPS continues reporting. Forecast; inverters online and producing normally as of Jun 9 at 8 | 0 | 6 | 1506 | All 24 inverters online and producing normally as of Jun 9 at 8:08 PM EDT, with the site tracking expected output closely through the afternoon on the production and expected chart. Clear skies, 77Â°F, light winds. 30-day Energy Performance Index averages 0.96 with inverter availability at 100%. Production totaled 812 MWh vs. 791 MWh estimate (103%). Sampled-inverter PV model losses and tracker losses (~7 kWh/day) are minor. Meter-to-inverter ratio is 0.98, normal. The rule tool flags excessiv
S65786 | Whitehall Solar | Unknown | Unknown | No | Yes | 2 | Medium | 2000 | 2000 |  |  |  |  | 8 | sensor calibration; inverter derating but no stow risk with light winds.; inverters online and producing as of Jun 9 at 8; weather station module-temp sensor reading below ambient â; tracker losses are negligible | 0 | 5 | 1505 | All 16 inverters online and producing as of Jun 9 at 8:08 PM EDT, with the site reaching ~2,000 kW peak hourly output earlier today per the production and expected chart. Light rain and variable cloud cover suppressed midday output today and on Jun 7â8, consistent with weather. 30-day Energy Performance Index averaged 0.92 and inverter availability averaged 100%. Sampled-inverter PV model losses show no major issues; tracker losses are negligible (~2â5 kWh/day). Meter-to-inverter ratio is
S65787 | Sunflower Solar | Unknown | Unknown | Yes | Yes | 3 | High | 9996 | 9996 |  |  |  |  | 10 | inverters are communicating and operating as of Jun 9 at 8; sensor and tracker alignment. Forecast is light rain with highs 93â; meter; weather station; tracker-error and POA insolation-mismatch flags | 0 | 4 | 1457 | All 80 inverters are communicating and operating as of Jun 9 at 8:09 PM EDT, with the production meter, weather station, and trackers reporting normally. Light rain is on site at 79Â°F, with reduced afternoon production today consistent with overcast conditions. No production events in the last two weeks. Daily output has tracked the site performance estimate closely, with full-capacity hours (~9,996 kW) observed Jun 3â5. 30-day EPI averages 0.97 and inverter availability is 99%. No major lo
S65788 | Gray Fox Solar | Unknown | Unknown | Yes | Yes | 3 | High | [6 empty] | 3 | inverters communicating as of Jun 9 at 8; inverter availability 97; inverter and tracker losses show nothing notable. Meter-to-inverter ratio is 0.98 | 0 | 5 | 1503 | All 40 inverters communicating as of Jun 9 at 8:09 PM EDT, with site producing through a light-rain afternoon. Today's peak hourly output reached ~4.9 MW around noon before clouds and rain reduced afternoon output, yielding a partial-day EPI of 0.68. Recent days track expected output closely. No production events in the last two weeks. Jun 8 and Jun 9 both saw weather-driven dips consistent with rain, not equipment issues. 30-day EPI averages 0.88 and inverter availability 97%. Production reac
S65918 | C & B Graham Energy | Partial / Issues | Unknown | Yes | Yes | 3 | High | 22830 | [5 empty] | 9 | metering data gap. Multiple; inverters are confirmed offline based on; weather station offline. Forecast; meter-to-inverter ratio on reporting meters; meter shows 22 | 0 | 4 | 1537 | Site producing through evening with light rain; meter shows 22,830 kWh today across METER 2 and METER 3. Several inverters are confirmed offline based on hourly production: INV-4 (since Jun 9 ~1 PM EDT, forced outage â Shutdown Command), INV-7 and INV-9 (since Jun 2, forced outages), INV-13 (since May 21), INV-17 (since Apr 22), INV-22 (Jun 9 ~5 PM, arc fault), INV-23 (since Apr 10), INV-35 (since Apr 6). INV-14 tripped Jun 9 7:21 AM (hardware self-test) but resumed. Combined ~1.4 MW offline;
S66000 | Auburn Solar | All Communicating | Unknown | Yes | Yes | 1 | Low | 13 | [5 empty] | 6 | pyranometer calibration drift worth reviewing.; meter configuration. No active alerts and rule tool is clean. Forecast; Inverter 1 producing normally through the afternoon under light rain conditions. Today; Tracker losses; Meter-to-inverter ratio is 1.01 | 0 | 4 | 1396 | All hardware is communicating as of Jun 9 at 5:09 PM PDT, with Inverter 1 producing normally through the afternoon under light rain conditions. Today's production tracks expected output closely, peaking near 2.0 MW. Over the last 30 days, the site is performing well: EPI averages 1.09 and inverter availability is 100%. Total production of 553 MWh is 123% of estimate. The persistently elevated EPI (>1.1 on several days) suggests a possible PV model or pyranometer calibration drift worth reviewi
S66001 | Sheridan Solar | Unknown | Unknown | No | Yes | 3 | High | 25 | [5 empty] | 7 | Meter-to-inverter ratio is 0.99; tracker losses are minimal; weather station temperature â; Inverter 1 is online and producing; sensor calibration but no production impact. Forecast | 0 | 4 | 1247 | Inverter 1 is online and producing, with hardware last update at Jun 9 at 5:09 PM PDT. Current conditions are light rain at 59Â°F, and today's production reached ~2.5 MW at midday under variable irradiance. 30-day Energy Performance Index averages 1.02 and inverter availability is 100%. Total production of 829 MWh is 114% of estimate. No major losses identified on the sampled inverter; tracker losses are minimal (<25 kWh/day). Meter-to-inverter ratio is 0.99 (normal). The rule tool flagged a h
S66930 | Elk Solar | Partial / Issues | Unknown | No | Yes | 3 | High | 750 | [5 empty] | 10 | tracker losses; metering issue.; meter; Inverter 01.15 also shows zero production with stuck AC telemetry â; Inverters 01.01 and 01.05 show low energy ratios | 1 | 6 | 1762 | Inverter 01.02 has been offline since May 27 at 3:29 AM EDT (forced outage, ~750 kWh/day downtime loss on sampled inverter). Inverter 01.15 also shows zero production with stuck AC telemetry â concurrent outage. Inverters 01.08â01.14 show reduced availability ~30% with ~575â633 kWh/day downtime loss each. Combined ~9 inverter outage represents ~1.1 MW affected capacity, ~5.6 MWh/day loss, ~78 MWh over 14 days. Today's site peak was ~4.3 MW around noon under light rain; weather-limited.
S68112 | Wallace Solar | Unknown | Unknown | Yes | Yes | 3 | High | 59 | [5 empty] | 6 | Tracker losses were minimal; Meter-to-inverter ratio is 0.99; Inverter availability; Inverter 1 is online and producing; pyranometer azimuth | 1 | 5 | 1355 | Inverter 1 is online and producing, with the hardware last reporting at 5:07 PM PDT on Jun 9. Light rain is reducing output today, with a peak hourly output of ~2.4 MWh this morning per the production chart. No production events in the last 30 days. Inverter availability held at 100%. The 30-day EPI averaged 1.07, persistently above 1.0, suggesting a PV model or POA calibration issue rather than a plant problem. Tracker losses were minimal (~0.9â59 kWh/day). Meter-to-inverter ratio is 0.99,
S68113 | Marble Solar | All Communicating | Unknown | Yes | Yes | 0 | Clean | 26 | [5 empty] | 5 | tracker losses; Meter-to-inverter ratio is 0.99; Inverter 1 produced about 2.6 MW peak earlier today under clear skies and 61Â; inverter availability at 100; inverter | 0 | 5 | 1473 | Marble Solar is operating normally as of Jun 9 at 5:09 PM PDT. All hardware is communicating, and Inverter 1 produced about 2.6 MW peak earlier today under clear skies and 61Â°F temperatures. 30-day Energy Performance Index averages 0.99 with inverter availability at 100%. Total production of 758 MWh is 107% of estimate. No major losses identified in the PV model for the sampled inverter; tracker losses are minimal (under 26 kWh/day). Meter-to-inverter ratio is 0.99, within normal range. No ac
S70532 | Longleaf Pine Solar, LLC | Partial / Issues | Unknown | Yes | Yes | 3 | High | 30 | [5 empty] | 7 | Tracker Controller 1 has been offline since Jun 3 with minimal energy impact; tracker error per; meter chart; meter and inverter production both days visible on the; inverters are online and producing as of Jun 9 at 8 | 0 | 5 | 1640 | All 40 inverters are online and producing as of Jun 9 at 8:10 PM EDT, with site output tracking irradiance on a light-rain day per the production and expected chart. A site-wide outage occurred Jun 3â4, with zero meter and inverter production both days visible on the production meter chart. Cause is undetermined from available data. Estimated loss ~83 MWh (2 days, 100% capacity, ~42 MWh/day expected). Production fully recovered Jun 5. A similar full-site outage occurred May 17â19, contribu
S70645 | Williams Solar, LLC | Partial / Issues | Unknown | Yes | Yes | 3 | High | 125 | 125 |  |  |  |  | 6 | inverters are online and producing normally under clear skies. INVERTER A20 forced outage; inverter; meter-to-inverter ratio; INVERTER A20 has been offline since Jun 5 with zero production while peers operate normally. The; inverter availability | 0 | 5 | 1417 | INVERTER A20 has been offline since Jun 5 with zero production while peers operate normally. The meter-to-inverter ratio of 0.97 confirms a true outage, not a comm loss. A grid overvoltage fault on Jun 8 at 3:10 PM EDT followed by a device communication alert at 3:39 PM points to a forced outage. The other 39 inverters are online and producing normally under clear skies. INVERTER A20 forced outage (Jun 5âpresent, ongoing ~5 days, 125 kW / 2.5% of site capacity). Estimated loss ~5 MWh (5 days
S55935 | Manuel Lawrence Dairy | Unknown | Unknown | Yes | Yes | 3 | High | [6 empty] | 3 | Inverter derating is possible during peak afternoon hours later this week. Data retrieval should be restored to enable proper performance assessment.; tracker. These findings cannot be validated against meter-to-inverter ratio or production charts due to the data retrieval failures noted above. Forecast is clear and hot through Jun 12; inverter availability and is unable to calculate PV losses across all 15 CPS SCA 60KTL-DO inverters or energy ratio at the Elkor production meter. The IMT reference cell is also reporting invalid module temperature and irradiance | 1 | 1 | 1096 | Site status cannot be fully assessed â hardware list, production charts, availability, and EPI data are all unavailable for this reporting period. No active alerts are present. Current site time is Jun 9 at 5:11 PM PDT, with clear skies and 91Â°F. Conditions are favorable for production, but actual output cannot be confirmed from available data. The rule tool reports 0% inverter availability and is unable to calculate PV losses across all 15 CPS SCA 60KTL-DO inverters or energy ratio at the

## Urgency Ranking
site_key | site_name | urgency_label | comm_status | prod_status | has_active_alert | weather_impact | plain_text
S40834 | Green Elementary | High | Unknown | Unknown | Yes | Yes | All 11 Solectria PVI 28TL inverters, both meters, weather stations, and the gateway are communicating as of Jun 9 at 8:02 PM EDT. Today's production was limited by light rain, with peak hourly output near midday around 200 kWh site-wide. Over the last 30 days, the site averaged an Energy Performance Index of 0.88 with 100% inverter availability. 30-day production reached 92% of estimate. Sampled inverter losses show DC/AC age losses near 5% each and residual loss around 7%, consistent with a m
S40835 | Gallia Academy | High | Partial / Issues | Below Expected | Yes | Yes | Solectria Inverter - 1 has been offline since Apr 6 at 10:57 AM EDT, last upload confirms ~64 days down. Meter-to-inverter ratio today is ~1.06 â consistent with 1 of 20 inverters not producing, confirming an outage rather than comm loss. The remaining 19 inverters are producing today, with site output tracking expected energy under light rain (73Â°F). Inverter 12 shows ~29% residual loss versus peers â a persistent underperformance worth field review. Estimated loss from Inverter - 1: ~12
S44566 | RIT | High | Unknown | Unknown | No | Yes | All 27 inverters are online and producing as of Jun 9 at 8:04 PM EDT, with light rain and 72Â°F at site. Today's peak hourly output reached ~1.6 MW around midday, consistent with overcast conditions. The site is healthy. 30-day EPI averages ~1.10, and inverter availability is 94%, pulled down by reduced availability May 27â29 that has since fully recovered. 30-day production totaled 320 MWh vs. 334 MWh estimate (96%). Meter-to-inverter ratio is 0.99, normal. The persistently elevated EPI (~1
S55935 | Manuel Lawrence Dairy | High | Unknown | Unknown | Yes | Yes | Site status cannot be fully assessed â hardware list, production charts, availability, and EPI data are all unavailable for this reporting period. No active alerts are present. Current site time is Jun 9 at 5:11 PM PDT, with clear skies and 91Â°F. Conditions are favorable for production, but actual output cannot be confirmed from available data. The rule tool reports 0% inverter availability and is unable to calculate PV losses across all 15 CPS SCA 60KTL-DO inverters or energy ratio at the
S44882 | Monroe Landfill | High | Partial / Issues | Unknown | Yes | Yes | Inverter 20 has been offline since May 30, confirmed by an Insulation Resistance Low (IsolationErr) fault and stuck-at-zero AC telemetry. Classified as a forced outage affecting ~73 kW (~3.7% of site capacity), with ~2.3 MWh lost over 11 days (~210 kWh/day expected per the PV model losses for the sampled inverter). All other 26 inverters are online and producing in line with peers as of Jun 9 at 8:03 PM EDT. 30-day EPI averages 1.18 and inverter availability is 96%, the latter dragged by INV-20
S54553 | Butler Maple | High | All Communicating | Unknown | Yes | Yes | All hardware is communicating as of Jun 9 around 5:05 PM PDT, and SMA SC4000 Inverter-1 is producing normally, reaching ~3.4 MW midday under light rain conditions. Site is operating normally with no active production events. 30-day Energy Performance Index averages 1.01 and inverter availability is 100%. 30-day production is 1080 MWh, ~116% of estimate. Sampled-inverter PV model losses show typical DC/AC age (~3%) and soiling (~1%); no major losses identified. Tracker losses are negligible (<
S51958 | WCPS - Westwood Hills Elementary School | High | All Communicating | Unknown | Yes | Yes | All three inverters are online and producing as of Jun 9 at 6:00 PM EDT, with the production meter at 769.8 kWh today under light rain. Hardware is communicating normally. Current conditions (72Â°F, light rain) are consistent with the reduced afternoon output seen today. No production events occurred in the reporting window. The 30-day Energy Performance Index averaged 0.95 and inverter availability was 100%. Sampled-inverter PV model losses show routine AC/DC age (~3% each) and minor soiling
S63838 | Bulloch 1A | High | Unknown | Unknown | Yes | Yes | All 28 inverters online and reporting fresh telemetry as of Jun 9 at 8:07 PM EDT, with the site past sunset under clear 82Â°F skies. Earlier today the site reached ~3.0 MW around noon, consistent with AC capacity, though afternoon production was variable with passing clouds. Over the last 30 days, the site averaged an EPI of 0.98 and 99.9% inverter availability. Sampled-inverter PV model losses show only minor age and soiling losses; no major losses identified. Meter-to-inverter ratio is 0.98,
S63840 | Upson | High | Unknown | Unknown | Yes | No | All 24 inverters online and reporting as of Jun 9 at 8:07 PM EDT, with the site in post-sunset hours. Recent days have shown variable production consistent with mixed insolation; Jun 8 and Jun 9 ran well below clear-sky days earlier in the week per the production and expected chart. 30-day Energy Performance Index averages 0.96 with inverter availability at 100%. Sampled-inverter PV model losses show no notable items; tracker losses are under 1 kWh/day. Meter-to-inverter ratio is 0.98 over 30
S59656 | Whitetail | High | Unknown | Unknown | Yes | Yes | All 80 SunGrow inverters online and reporting as of Jun 9 at 8:06 PM EDT, with the site producing normally through the day under light rain. Current weather is 77Â°F with light rain; peak hourly output reached ~9.4 MW around midday per the production and expected chart. 30-day EPI averages 0.94 and inverter availability 99%. Production-to-estimate ratio is 91%. Sampled-inverter PV model losses show no major losses; tracker lost energy is 0 kWh over 7 days. Meter-to-inverter ratio is 0.99 (norm
S54681 | Eagle | High | Unknown | Unknown | Yes | Yes | All 24 CPS SCH125kTL inverters are online and producing in line with peers as of Jun 9 at 8:06 PM EDT, with current output tapering normally near sunset under light rain. Inv-8 shows a persistent ~25% deficit vs. peers (capped near 75 kW during midday hours) visible across recent days in the production chart, coincident with an active External Fan Err fault triggered Jun 9 at 3:42 PM. Classify as partial capability on ~125 kW (~3% of site); ongoing impact ~150 kWh/day. 30-day EPI averages 0.97
S64602 | McLean | High | Partial / Issues | Unknown | Yes | Yes | All 40 inverters communicating as of Jun 9 at 8:07 PM EDT, with the most recent uploads within minutes. Site is producing under light rain after a cloudy afternoon; peak output today reached ~4.7 MW around 11 AM. 30-day Energy Performance Index averages 0.93 with no major drops, and inverter availability is 100% in the past week (site 30-day: 99.83%). No notable PV model losses on the sampled inverter; tracker lost energy runs ~50â125 kWh/day, a minor performance drag tied to several stuck/er
S66930 | Elk Solar | High | Partial / Issues | Unknown | No | Yes | Inverter 01.02 has been offline since May 27 at 3:29 AM EDT (forced outage, ~750 kWh/day downtime loss on sampled inverter). Inverter 01.15 also shows zero production with stuck AC telemetry â concurrent outage. Inverters 01.08â01.14 show reduced availability ~30% with ~575â633 kWh/day downtime loss each. Combined ~9 inverter outage represents ~1.1 MW affected capacity, ~5.6 MWh/day loss, ~78 MWh over 14 days. Today's site peak was ~4.3 MW around noon under light rain; weather-limited.
S68112 | Wallace Solar | High | Unknown | Unknown | Yes | Yes | Inverter 1 is online and producing, with the hardware last reporting at 5:07 PM PDT on Jun 9. Light rain is reducing output today, with a peak hourly output of ~2.4 MWh this morning per the production chart. No production events in the last 30 days. Inverter availability held at 100%. The 30-day EPI averaged 1.07, persistently above 1.0, suggesting a PV model or POA calibration issue rather than a plant problem. Tracker losses were minimal (~0.9â59 kWh/day). Meter-to-inverter ratio is 0.99,
S65918 | C & B Graham Energy | High | Partial / Issues | Unknown | Yes | Yes | Site producing through evening with light rain; meter shows 22,830 kWh today across METER 2 and METER 3. Several inverters are confirmed offline based on hourly production: INV-4 (since Jun 9 ~1 PM EDT, forced outage â Shutdown Command), INV-7 and INV-9 (since Jun 2, forced outages), INV-13 (since May 21), INV-17 (since Apr 22), INV-22 (Jun 9 ~5 PM, arc fault), INV-23 (since Apr 10), INV-35 (since Apr 6). INV-14 tripped Jun 9 7:21 AM (hardware self-test) but resumed. Combined ~1.4 MW offline;
S65787 | Sunflower Solar | High | Unknown | Unknown | Yes | Yes | All 80 inverters are communicating and operating as of Jun 9 at 8:09 PM EDT, with the production meter, weather station, and trackers reporting normally. Light rain is on site at 79Â°F, with reduced afternoon production today consistent with overcast conditions. No production events in the last two weeks. Daily output has tracked the site performance estimate closely, with full-capacity hours (~9,996 kW) observed Jun 3â5. 30-day EPI averages 0.97 and inverter availability is 99%. No major lo
S65788 | Gray Fox Solar | High | Unknown | Unknown | Yes | Yes | All 40 inverters communicating as of Jun 9 at 8:09 PM EDT, with site producing through a light-rain afternoon. Today's peak hourly output reached ~4.9 MW around noon before clouds and rain reduced afternoon output, yielding a partial-day EPI of 0.68. Recent days track expected output closely. No production events in the last two weeks. Jun 8 and Jun 9 both saw weather-driven dips consistent with rain, not equipment issues. 30-day EPI averages 0.88 and inverter availability 97%. Production reac
S65216 | Green Solar | High | Partial / Issues | Unknown | No | Yes | Inverter 1 is online and producing, last reporting at 5:05 PM PDT on Jun 9, with all other hardware communicating normally. Current output is tracking expected energy closely under clear skies and 57Â°F. No production events occurred in the reporting period. Variable output on Jun 3, Jun 5, and Jun 8 reflects intermittent cloud cover, not equipment issues. 30-day Energy Performance Index averaged 0.99 with inverter availability at 99%. Production reached 99% of estimate. No major losses identi
S64603 | Shorthorn | High | Partial / Issues | Unknown | Yes | Yes | All 72 inverters communicating as of Jun 9 at 8:08 PM EDT, with production tapering normally into evening under light rain. Conditions are intermittently cloudy, consistent with reduced midday output today. No production events in the reporting window. A brief site dip on Jun 5 (EPI 0.81, availability 88%) recovered the same day. 30-day EPI averages 0.97 with inverter availability at 99%. Sampled-inverter losses and tracker losses are minor. Meter-to-inverter ratio is 0.98 (normal). Open trac
S70532 | Longleaf Pine Solar, LLC | High | Partial / Issues | Unknown | Yes | Yes | All 40 inverters are online and producing as of Jun 9 at 8:10 PM EDT, with site output tracking irradiance on a light-rain day per the production and expected chart. A site-wide outage occurred Jun 3â4, with zero meter and inverter production both days visible on the production meter chart. Cause is undetermined from available data. Estimated loss ~83 MWh (2 days, 100% capacity, ~42 MWh/day expected). Production fully recovered Jun 5. A similar full-site outage occurred May 17â19, contribu
S70645 | Williams Solar, LLC | High | Partial / Issues | Unknown | Yes | Yes | INVERTER A20 has been offline since Jun 5 with zero production while peers operate normally. The meter-to-inverter ratio of 0.97 confirms a true outage, not a comm loss. A grid overvoltage fault on Jun 8 at 3:10 PM EDT followed by a device communication alert at 3:39 PM points to a forced outage. The other 39 inverters are online and producing normally under clear skies. INVERTER A20 forced outage (Jun 5âpresent, ongoing ~5 days, 125 kW / 2.5% of site capacity). Estimated loss ~5 MWh (5 days
S66001 | Sheridan Solar | High | Unknown | Unknown | No | Yes | Inverter 1 is online and producing, with hardware last update at Jun 9 at 5:09 PM PDT. Current conditions are light rain at 59Â°F, and today's production reached ~2.5 MW at midday under variable irradiance. 30-day Energy Performance Index averages 1.02 and inverter availability is 100%. Total production of 829 MWh is 114% of estimate. No major losses identified on the sampled inverter; tracker losses are minimal (<25 kWh/day). Meter-to-inverter ratio is 0.99 (normal). The rule tool flagged a h
S40836 | Rio Grande Elementary | Medium | Unknown | Below Expected | No | Yes | All 13 Solectria 28kW inverters online and producing as of Jun 9 at 8:02 PM EDT, with the site in light rain and near sunset. Recent production tracks reduced expected output under cloudy conditions, with no outages observed. 30-day Energy Performance Index averages 0.88 and inverter availability is 100%. Site produced 53.0 MWh against 58.1 MWh estimate (91%) per the production meter. Sampled-inverter PV model losses show DC/AC age (~5% each) and ~10% residual; no major events identified. Mete
S51957 | WCPS - William Perry Elementary School | Medium | Unknown | Below Expected | Yes | Yes | All three CPS SCA60KTL inverters are online and producing as of Jun 9 at 7:38 PM EDT, with the production meter and weather station reporting normally. Today's peak hourly output was modest (~130 kW combined around midday) under variable rain conditions, consistent with the Light rain currently at the site. The site has been underperforming throughout the 30-day window. The Energy Performance Index averages roughly 0.41, with inverter availability at 100% and 30-day production of 29,929 kWh vs
S44485 | RRH 1 & 2 | Medium | Unknown | Unknown | Yes | Yes | All 66 inverters online and producing normally as of Jun 9 at 8:04 PM EDT, with site output tracking expected through the day on production vs. expected. Current conditions are light rain at 70Â°F. 30-day Energy Performance Index averages 1.05, with several days in the 1.11â1.16 range suggesting possible PV model or POA sensor calibration drift worth review. Inverter availability is 100%. Sampled-inverter PV model losses show no notable issues beyond normal age and inverter losses. Meter-to
S51959 | WCPS - Waynesboro High School | Medium | Unknown | Unknown | Yes | Yes | Both inverters are online and producing as of Jun 9 at 7:07 PM EDT, with the site generating 590 kWh today under light rain and overcast conditions. Today's peak hourly output reached ~97 kW around 2:00 PM, consistent with the cloudy weather. Over the last 30 days, the Energy Performance Index averaged 0.84 and inverter availability held at 100%. Production totaled 18.4 MWh, or 90% of the estimate. PV model losses for the sampled inverter show ~4% soiling and a large negative residual, suggesti
S51960 | WCPS - Kate Collins Middle School | Medium | Unknown | Below Expected | No | Yes | All 5 CPS SCA60KTL inverters online and producing as of Jun 9 at 6:00 PM EDT under light rain. Today's peak hourly output was ~215 kW around 2:00 PM, consistent with overcast conditions. 30-day Energy Performance Index averages 0.78 with inverter availability at 100%. Production totals 44.5 MWh vs. 56.9 MWh estimated (78%), reflecting frequent rain in the period rather than a discrete event. Inverters 2 and 3 consistently produce ~30â35% less than Inverter 1 across every daylight hour, flagg
S65786 | Whitehall Solar | Medium | Unknown | Unknown | No | Yes | All 16 inverters online and producing as of Jun 9 at 8:08 PM EDT, with the site reaching ~2,000 kW peak hourly output earlier today per the production and expected chart. Light rain and variable cloud cover suppressed midday output today and on Jun 7â8, consistent with weather. 30-day Energy Performance Index averaged 0.92 and inverter availability averaged 100%. Sampled-inverter PV model losses show no major issues; tracker losses are negligible (~2â5 kWh/day). Meter-to-inverter ratio is
S63837 | Bulloch 1B | Medium | Unknown | Unknown | Yes | Yes | All 24 inverters online and reporting as of Jun 9 at 8:07 PM EDT, with the site producing 24,000 kWh today against a 24,475 kWh estimate. Current conditions are clear and 82Â°F at sunset, so production is finished for the day. 30-day Energy Performance Index averages 0.99 with inverter availability at 100% over the last 10 days. PV model losses on the sampled inverter show no major issues; tracker lost energy averages ~76 kWh/day, minor. Meter-to-inverter ratio is 0.98, normal. The rule tool
S54613 | Warbler | Medium | Unknown | Below Expected | Yes | Yes | All 32 Sungrow SG125 inverters are online and communicating as of Jun 9 at 8:06 PM EDT, with all balance-of-plant devices reporting normally. Today's production was limited by cloud cover; recent clear days (Jun 3â5) reached the 4 MW AC cap during midday hours per the production and expected chart. No discrete production events in the last two weeks. Day-to-day variability on May 22â26 and Jun 1â2 aligns with weather, not equipment issues. 30-day Energy Performance Index averaged 0.88 an
S65784 | Washington Solar | Medium | Unknown | Unknown | No | Yes | All 40 inverters communicating as of Jun 9 at 8:08 PM EDT, with site availability at 100% over the last 30 days. Current conditions are light rain at 77Â°F, and today's production reflects a cloudy/rainy profile, peaking near 3.7 MW at 1:00 PM versus ~5 MW expected. The INVERTER 6 invalid-data warning that triggered at 8:03 PM is a brief end-of-day comm blip; Last Update is current. The 30-day Energy Performance Index averages ~1.16, consistently above 1.1, suggesting a PV model or POA sensor
S65785 | Harding Solar | Medium | Unknown | Unknown | Yes | Yes | All 24 inverters online and producing normally as of Jun 9 at 8:08 PM EDT, with the site tracking expected output closely through the afternoon on the production and expected chart. Clear skies, 77Â°F, light winds. 30-day Energy Performance Index averages 0.96 with inverter availability at 100%. Production totaled 812 MWh vs. 791 MWh estimate (103%). Sampled-inverter PV model losses and tracker losses (~7 kWh/day) are minor. Meter-to-inverter ratio is 0.98, normal. The rule tool flags excessiv
S63839 | Richmond | Low | Unknown | On Track | No | Yes | All 24 inverters online and producing as of Jun 9 at 8:07 PM EDT, with clear skies and 82Â°F. Current-day production is tracking expected output closely, with a peak around 2.6 MW midday. 30-day Energy Performance Index averages 0.99 and inverter availability is 100% over the last 9 days (site 30-day 99.7%). Sampled-inverter PV model losses show no notable findings; tracker losses are minor (~30â55 kWh/day). Meter-to-inverter ratio is 0.98, normal. The rule tool flags two NCU 1 trackers stuc
S66000 | Auburn Solar | Low | All Communicating | Unknown | Yes | Yes | All hardware is communicating as of Jun 9 at 5:09 PM PDT, with Inverter 1 producing normally through the afternoon under light rain conditions. Today's production tracks expected output closely, peaking near 2.0 MW. Over the last 30 days, the site is performing well: EPI averages 1.09 and inverter availability is 100%. Total production of 553 MWh is 123% of estimate. The persistently elevated EPI (>1.1 on several days) suggests a possible PV model or pyranometer calibration drift worth reviewi
S68113 | Marble Solar | Clean | All Communicating | Unknown | Yes | Yes | Marble Solar is operating normally as of Jun 9 at 5:09 PM PDT. All hardware is communicating, and Inverter 1 produced about 2.6 MW peak earlier today under clear skies and 61Â°F temperatures. 30-day Energy Performance Index averages 0.99 with inverter availability at 100%. Total production of 758 MWh is 107% of estimate. No major losses identified in the PV model for the sampled inverter; tracker losses are minimal (under 26 kWh/day). Meter-to-inverter ratio is 0.99, within normal range. No ac

## Numeric Values
site_key | site_name | production_kwh | power_kw | pct_expected | perf_index | temp_f | pct_loss
S40834 | Green Elementary | 200
S40835 | Gallia Academy | 200
S40836 | Rio Grande Elementary | 28 | 28
S44485 | RRH 1 & 2
S44566 | RIT
S44882 | Monroe Landfill | 73 | 73
S51957 | WCPS - William Perry Elementary School | 130 | 130
S51958 | WCPS - Westwood Hills Elementary School | 769.8
S51959 | WCPS - Waynesboro High School | 590 | 97
S51960 | WCPS - Kate Collins Middle School | 215 | 215 |  |  |  | 35
S54553 | Butler Maple | 4
S54613 | Warbler
S54681 | Eagle | 75 | 75
S59656 | Whitetail | 0
S63837 | Bulloch 1B | 24000
S63838 | Bulloch 1A | 24
S63839 | Richmond | 55
S63840 | Upson | 1
S64602 | McLean | 125
S64603 | Shorthorn
S65216 | Green Solar
S65784 | Washington Solar | 3
S65785 | Harding Solar | 7
S65786 | Whitehall Solar | 2000 | 2000
S65787 | Sunflower Solar | 9996 | 9996
S65788 | Gray Fox Solar
S65918 | C & B Graham Energy | 22830
S66000 | Auburn Solar | 13
S66001 | Sheridan Solar | 25
S66930 | Elk Solar | 750
S68112 | Wallace Solar | 59
S68113 | Marble Solar | 26
S70532 | Longleaf Pine Solar, LLC | 30
S70645 | Williams Solar, LLC | 125 | 125
S55935 | Manuel Lawrence Dairy

## Chart URLs
site_key | site_name | url | hw_key | section | start | end | bin | columns | hardware_h
S40834 | Green Elementary | https://apps.alsoenergy.com/powertrack/S40834/analysis/chartbuilder?c=79&start=2026-05-10T20:04:02&end=2026-06-09T20:04:02&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:04:02 | 2026-06-09T20:04:02 | 1440 | 79 | 2*5*11
S40834 | Green Elementary | https://apps.alsoenergy.com/powertrack/S40834/analysis/chartbuilder?c=259&start=2026-05-10T20:04:02&end=2026-06-09T20:04:02&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:04:02 | 2026-06-09T20:04:02 | 1440 | 259 | 1*5*11
S40834 | Green Elementary | https://apps.alsoenergy.com/powertrack/S40834/analysis/chartbuilder?c=72&start=2026-05-10T20:04:02&end=2026-06-09T20:04:02&bin=1440&h=1*5*H119162 |  | chartbuilder | 2026-05-10T20:04:02 | 2026-06-09T20:04:02 | 1440 | 72 | 1*5*H119162
S40835 | Gallia Academy | https://apps.alsoenergy.com/powertrack/S40835/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S40835 | Gallia Academy | https://apps.alsoenergy.com/powertrack/S40835/analysis/chartbuilder?c=72&start=2026-05-10T20:04:12&end=2026-06-09T20:04:12&bin=1440&h=1*5*H119285 |  | chartbuilder | 2026-05-10T20:04:12 | 2026-06-09T20:04:12 | 1440 | 72 | 1*5*H119285
S40835 | Gallia Academy | https://apps.alsoenergy.com/powertrack/S40835/analysis/chartbuilder?c=79&start=2026-05-10T20:04:12&end=2026-06-09T20:04:12&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:04:12 | 2026-06-09T20:04:12 | 1440 | 79 | 2*5*11
S40835 | Gallia Academy | https://apps.alsoenergy.com/powertrack/S40835/analysis/chartbuilder?c=259&start=2026-05-10T20:04:12&end=2026-06-09T20:04:12&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:04:12 | 2026-06-09T20:04:12 | 1440 | 259 | 1*5*11
S40835 | Gallia Academy | https://apps.alsoenergy.com/powertrack/S40835/operations/alerts |  | alerts
S40836 | Rio Grande Elementary | https://apps.alsoenergy.com/powertrack/S40836/analysis/chartbuilder?c=79&start=2026-05-10T20:04:26&end=2026-06-09T20:04:26&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:04:26 | 2026-06-09T20:04:26 | 1440 | 79 | 2*5*11
S40836 | Rio Grande Elementary | https://apps.alsoenergy.com/powertrack/S40836/analysis/chartbuilder?c=259&start=2026-05-10T20:04:26&end=2026-06-09T20:04:26&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:04:26 | 2026-06-09T20:04:26 | 1440 | 259 | 1*5*11
S40836 | Rio Grande Elementary | https://apps.alsoenergy.com/powertrack/S40836/analysis/chartbuilder?c=15&start=2026-05-10T20:04:26&end=2026-06-09T20:04:26&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:04:26 | 2026-06-09T20:04:26 | 1440 | 15 | 1*2*5*11
S40836 | Rio Grande Elementary | https://apps.alsoenergy.com/powertrack/S40836/analysis/chartbuilder?c=72&start=2026-05-10T20:04:26&end=2026-06-09T20:04:26&bin=1440&h=1*5*H119250 |  | chartbuilder | 2026-05-10T20:04:26 | 2026-06-09T20:04:26 | 1440 | 72 | 1*5*H119250
S40836 | Rio Grande Elementary | https://apps.alsoenergy.com/powertrack/S40836/analysis/ruletool |  | ruletool
S44485 | RRH 1 & 2 | https://apps.alsoenergy.com/powertrack/S44485/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S44485 | RRH 1 & 2 | https://apps.alsoenergy.com/powertrack/S44485/analysis/chartbuilder?c=79&start=2026-05-10T20:04:38&end=2026-06-09T20:04:38&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:04:38 | 2026-06-09T20:04:38 | 1440 | 79 | 2*5*11
S44485 | RRH 1 & 2 | https://apps.alsoenergy.com/powertrack/S44485/analysis/chartbuilder?c=259&start=2026-05-10T20:04:38&end=2026-06-09T20:04:38&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:04:38 | 2026-06-09T20:04:38 | 1440 | 259 | 1*5*11
S44485 | RRH 1 & 2 | https://apps.alsoenergy.com/powertrack/S44485/operations/alerts |  | alerts
S44566 | RIT | https://apps.alsoenergy.com/powertrack/S44566/analysis/chartbuilder?c=79&start=2026-05-10T20:04:53&end=2026-06-09T20:04:53&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:04:53 | 2026-06-09T20:04:53 | 1440 | 79 | 2*5*11
S44566 | RIT | https://apps.alsoenergy.com/powertrack/S44566/analysis/chartbuilder?c=259&start=2026-05-10T20:04:53&end=2026-06-09T20:04:53&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:04:53 | 2026-06-09T20:04:53 | 1440 | 259 | 1*5*11
S44566 | RIT | https://apps.alsoenergy.com/powertrack/S44566/analysis/chartbuilder?c=15&start=2026-05-10T20:04:53&end=2026-06-09T20:04:53&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:04:53 | 2026-06-09T20:04:53 | 1440 | 15 | 1*2*5*11
S44566 | RIT | https://apps.alsoenergy.com/powertrack/S44566/analysis/chartbuilder?c=72&start=2026-05-10T20:04:53&end=2026-06-09T20:04:53&bin=1440&h=1*5*H143483 |  | chartbuilder | 2026-05-10T20:04:53 | 2026-06-09T20:04:53 | 1440 | 72 | 1*5*H143483
S44566 | RIT | https://apps.alsoenergy.com/powertrack/S44566/analysis/ruletool |  | ruletool
S44882 | Monroe Landfill | https://apps.alsoenergy.com/powertrack/S44882/operations/alerts |  | alerts
S44882 | Monroe Landfill | https://apps.alsoenergy.com/powertrack/S44882/analysis/chartbuilder?c=72&start=2026-05-10T20:05:06&end=2026-06-09T20:05:06&bin=1440&h=1*5*H155958 |  | chartbuilder | 2026-05-10T20:05:06 | 2026-06-09T20:05:06 | 1440 | 72 | 1*5*H155958
S44882 | Monroe Landfill | https://apps.alsoenergy.com/powertrack/S44882/analysis/chartbuilder?c=79&start=2026-05-10T20:05:06&end=2026-06-09T20:05:06&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:05:06 | 2026-06-09T20:05:06 | 1440 | 79 | 2*5*11
S44882 | Monroe Landfill | https://apps.alsoenergy.com/powertrack/S44882/analysis/chartbuilder?c=259&start=2026-05-10T20:05:06&end=2026-06-09T20:05:06&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:05:06 | 2026-06-09T20:05:06 | 1440 | 259 | 1*5*11
S44882 | Monroe Landfill | https://apps.alsoenergy.com/powertrack/S44882/analysis/ruletool |  | ruletool
S51957 | WCPS - William Perry Elementary School | https://apps.alsoenergy.com/powertrack/S51957/analysis/chartbuilder?c=79&start=2026-05-10T20:05:18&end=2026-06-09T20:05:18&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:05:18 | 2026-06-09T20:05:18 | 1440 | 79 | 2*5*11
S51957 | WCPS - William Perry Elementary School | https://apps.alsoenergy.com/powertrack/S51957/analysis/chartbuilder?c=259&start=2026-05-10T20:05:18&end=2026-06-09T20:05:18&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:05:18 | 2026-06-09T20:05:18 | 1440 | 259 | 1*5*11
S51957 | WCPS - William Perry Elementary School | https://apps.alsoenergy.com/powertrack/S51957/analysis/chartbuilder?c=72&start=2026-05-10T20:05:18&end=2026-06-09T20:05:18&bin=1440&h=1*5*H226501 |  | chartbuilder | 2026-05-10T20:05:18 | 2026-06-09T20:05:18 | 1440 | 72 | 1*5*H226501
S51957 | WCPS - William Perry Elementary School | https://apps.alsoenergy.com/powertrack/S51957/analysis/ruletool |  | ruletool
S51957 | WCPS - William Perry Elementary School | https://apps.alsoenergy.com/powertrack/S51957/operations/alerts |  | alerts
S51958 | WCPS - Westwood Hills Elementary School | https://apps.alsoenergy.com/powertrack/S51958/analysis/chartbuilder?c=15&start=2026-05-10T20:05:29&end=2026-06-09T20:05:29&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:05:29 | 2026-06-09T20:05:29 | 1440 | 15 | 1*2*5*11
S51958 | WCPS - Westwood Hills Elementary School | https://apps.alsoenergy.com/powertrack/S51958/analysis/chartbuilder?c=79&start=2026-05-10T20:05:29&end=2026-06-09T20:05:29&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:05:29 | 2026-06-09T20:05:29 | 1440 | 79 | 2*5*11
S51958 | WCPS - Westwood Hills Elementary School | https://apps.alsoenergy.com/powertrack/S51958/analysis/chartbuilder?c=259&start=2026-05-10T20:05:29&end=2026-06-09T20:05:29&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:05:29 | 2026-06-09T20:05:29 | 1440 | 259 | 1*5*11
S51958 | WCPS - Westwood Hills Elementary School | https://apps.alsoenergy.com/powertrack/S51958/analysis/chartbuilder?c=72&start=2026-05-10T20:05:29&end=2026-06-09T20:05:29&bin=1440&h=1*5*H226494 |  | chartbuilder | 2026-05-10T20:05:29 | 2026-06-09T20:05:29 | 1440 | 72 | 1*5*H226494
S51958 | WCPS - Westwood Hills Elementary School | https://apps.alsoenergy.com/powertrack/S51958/analysis/ruletool |  | ruletool
S51959 | WCPS - Waynesboro High School | https://apps.alsoenergy.com/powertrack/S51959/analysis/chartbuilder?c=79&start=2026-05-10T20:05:40&end=2026-06-09T20:05:40&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:05:40 | 2026-06-09T20:05:40 | 1440 | 79 | 2*5*11
S51959 | WCPS - Waynesboro High School | https://apps.alsoenergy.com/powertrack/S51959/analysis/chartbuilder?c=259&start=2026-05-10T20:05:40&end=2026-06-09T20:05:40&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:05:40 | 2026-06-09T20:05:40 | 1440 | 259 | 1*5*11
S51959 | WCPS - Waynesboro High School | https://apps.alsoenergy.com/powertrack/S51959/analysis/chartbuilder?c=72&start=2026-05-10T20:05:40&end=2026-06-09T20:05:40&bin=1440&h=1*5*H226508 |  | chartbuilder | 2026-05-10T20:05:40 | 2026-06-09T20:05:40 | 1440 | 72 | 1*5*H226508
S51959 | WCPS - Waynesboro High School | https://apps.alsoenergy.com/powertrack/S51959/operations/alerts |  | alerts
S51960 | WCPS - Kate Collins Middle School | https://apps.alsoenergy.com/powertrack/S51960/analysis/chartbuilder?c=79&start=2026-05-10T20:05:52&end=2026-06-09T20:05:52&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:05:52 | 2026-06-09T20:05:52 | 1440 | 79 | 2*5*11
S51960 | WCPS - Kate Collins Middle School | https://apps.alsoenergy.com/powertrack/S51960/analysis/chartbuilder?c=259&start=2026-05-10T20:05:52&end=2026-06-09T20:05:52&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:05:52 | 2026-06-09T20:05:52 | 1440 | 259 | 1*5*11
S51960 | WCPS - Kate Collins Middle School | https://apps.alsoenergy.com/powertrack/S51960/analysis/chartbuilder?c=15&start=2026-05-10T20:05:52&end=2026-06-09T20:05:52&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:05:52 | 2026-06-09T20:05:52 | 1440 | 15 | 1*2*5*11
S51960 | WCPS - Kate Collins Middle School | https://apps.alsoenergy.com/powertrack/S51960/analysis/ruletool |  | ruletool
S51960 | WCPS - Kate Collins Middle School | https://apps.alsoenergy.com/powertrack/S51960/analysis/chartbuilder?c=72&start=2026-05-10T20:05:52&end=2026-06-09T20:05:52&bin=1440&h=1*5*H226526 |  | chartbuilder | 2026-05-10T20:05:52 | 2026-06-09T20:05:52 | 1440 | 72 | 1*5*H226526
S54553 | Butler Maple | https://apps.alsoenergy.com/powertrack/S54553/analysis/chartbuilder?c=79&start=2026-05-10T17:06:04&end=2026-06-09T17:06:04&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T17:06:04 | 2026-06-09T17:06:04 | 1440 | 79 | 2*5*11
S54553 | Butler Maple | https://apps.alsoenergy.com/powertrack/S54553/analysis/chartbuilder?c=259&start=2026-05-10T17:06:04&end=2026-06-09T17:06:04&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T17:06:04 | 2026-06-09T17:06:04 | 1440 | 259 | 1*5*11
S54553 | Butler Maple | https://apps.alsoenergy.com/powertrack/S54553/analysis/chartbuilder?c=15&start=2026-05-10T17:06:04&end=2026-06-09T17:06:04&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T17:06:04 | 2026-06-09T17:06:04 | 1440 | 15 | 1*2*5*11
S54553 | Butler Maple | https://apps.alsoenergy.com/powertrack/S54553/analysis/chartbuilder?c=72&start=2026-05-10T17:06:04&end=2026-06-09T17:06:04&bin=1440&h=1*5*H262728 |  | chartbuilder | 2026-05-10T17:06:04 | 2026-06-09T17:06:04 | 1440 | 72 | 1*5*H262728
S54553 | Butler Maple | https://apps.alsoenergy.com/powertrack/S54553/analysis/chartbuilder?c=206&start=2026-06-02T17:06:04&end=2026-06-09T17:06:04&bin=1440&h=24&p=%5b%7b%22id%22%3a59%2c%22value%22%3atrue%7d%2c%7b%22id%22%3a |  | chartbuilder | 2026-06-02T17:06:04 | 2026-06-09T17:06:04 | 1440 | 206 | 24
S54553 | Butler Maple | https://apps.alsoenergy.com/powertrack/S54553/analysis/ruletool |  | ruletool
S54613 | Warbler | https://apps.alsoenergy.com/powertrack/S54613/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S54613 | Warbler | https://apps.alsoenergy.com/powertrack/S54613/analysis/chartbuilder?c=79&start=2026-05-10T20:06:16&end=2026-06-09T20:06:16&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:06:16 | 2026-06-09T20:06:16 | 1440 | 79 | 2*5*11
S54613 | Warbler | https://apps.alsoenergy.com/powertrack/S54613/analysis/chartbuilder?c=259&start=2026-05-10T20:06:16&end=2026-06-09T20:06:16&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:06:16 | 2026-06-09T20:06:16 | 1440 | 259 | 1*5*11
S54613 | Warbler | https://apps.alsoenergy.com/powertrack/S54613/analysis/chartbuilder?c=72&start=2026-05-10T20:06:16&end=2026-06-09T20:06:16&bin=1440&h=1*5*H263557 |  | chartbuilder | 2026-05-10T20:06:16 | 2026-06-09T20:06:16 | 1440 | 72 | 1*5*H263557
S54613 | Warbler | https://apps.alsoenergy.com/powertrack/S54613/analysis/ruletool |  | ruletool
S54681 | Eagle | https://apps.alsoenergy.com/powertrack/S54681/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S54681 | Eagle | https://apps.alsoenergy.com/powertrack/S54681/operations/alerts |  | alerts
S54681 | Eagle | https://apps.alsoenergy.com/powertrack/S54681/analysis/chartbuilder?c=79&start=2026-05-10T20:06:29&end=2026-06-09T20:06:29&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:06:29 | 2026-06-09T20:06:29 | 1440 | 79 | 2*5*11
S54681 | Eagle | https://apps.alsoenergy.com/powertrack/S54681/analysis/chartbuilder?c=259&start=2026-05-10T20:06:29&end=2026-06-09T20:06:29&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:06:29 | 2026-06-09T20:06:29 | 1440 | 259 | 1*5*11
S54681 | Eagle | https://apps.alsoenergy.com/powertrack/S54681/analysis/ruletool |  | ruletool
S59656 | Whitetail | https://apps.alsoenergy.com/powertrack/S59656/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S59656 | Whitetail | https://apps.alsoenergy.com/powertrack/S59656/analysis/chartbuilder?c=79&start=2026-05-10T20:06:42&end=2026-06-09T20:06:42&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:06:42 | 2026-06-09T20:06:42 | 1440 | 79 | 2*5*11
S59656 | Whitetail | https://apps.alsoenergy.com/powertrack/S59656/analysis/chartbuilder?c=259&start=2026-05-10T20:06:42&end=2026-06-09T20:06:42&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:06:42 | 2026-06-09T20:06:42 | 1440 | 259 | 1*5*11
S59656 | Whitetail | https://apps.alsoenergy.com/powertrack/S59656/analysis/chartbuilder?c=72&start=2026-05-10T20:06:42&end=2026-06-09T20:06:42&bin=1440&h=1*5*H312388 |  | chartbuilder | 2026-05-10T20:06:42 | 2026-06-09T20:06:42 | 1440 | 72 | 1*5*H312388
S59656 | Whitetail | https://apps.alsoenergy.com/powertrack/S59656/operations/alerts |  | alerts
S59656 | Whitetail | https://apps.alsoenergy.com/powertrack/S59656/analysis/ruletool |  | ruletool
S63837 | Bulloch 1B | https://apps.alsoenergy.com/powertrack/S63837/analysis/chartbuilder?c=79&start=2026-05-10T20:07:02&end=2026-06-09T20:07:02&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:07:02 | 2026-06-09T20:07:02 | 1440 | 79 | 2*5*11
S63837 | Bulloch 1B | https://apps.alsoenergy.com/powertrack/S63837/analysis/chartbuilder?c=259&start=2026-05-10T20:07:02&end=2026-06-09T20:07:02&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:07:02 | 2026-06-09T20:07:02 | 1440 | 259 | 1*5*11
S63837 | Bulloch 1B | https://apps.alsoenergy.com/powertrack/S63837/analysis/chartbuilder?c=72&start=2026-05-10T20:07:02&end=2026-06-09T20:07:02&bin=1440&h=1*5*H399338 |  | chartbuilder | 2026-05-10T20:07:02 | 2026-06-09T20:07:02 | 1440 | 72 | 1*5*H399338
S63837 | Bulloch 1B | https://apps.alsoenergy.com/powertrack/S63837/analysis/chartbuilder?c=206&start=2026-06-02T20:07:02&end=2026-06-09T20:07:02&bin=1440&h=24 |  | chartbuilder | 2026-06-02T20:07:02 | 2026-06-09T20:07:02 | 1440 | 206 | 24
S63837 | Bulloch 1B | https://apps.alsoenergy.com/powertrack/S63837/analysis/ruletool |  | ruletool
S63838 | Bulloch 1A | https://apps.alsoenergy.com/powertrack/S63838/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S63838 | Bulloch 1A | https://apps.alsoenergy.com/powertrack/S63838/analysis/chartbuilder?c=79&start=2026-05-10T20:07:14&end=2026-06-09T20:07:14&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:07:14 | 2026-06-09T20:07:14 | 1440 | 79 | 2*5*11
S63838 | Bulloch 1A | https://apps.alsoenergy.com/powertrack/S63838/analysis/chartbuilder?c=259&start=2026-05-10T20:07:14&end=2026-06-09T20:07:14&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:07:14 | 2026-06-09T20:07:14 | 1440 | 259 | 1*5*11
S63838 | Bulloch 1A | https://apps.alsoenergy.com/powertrack/S63838/analysis/chartbuilder?c=72&start=2026-05-10T20:07:14&end=2026-06-09T20:07:14&bin=1440&h=1*5*H400653 |  | chartbuilder | 2026-05-10T20:07:14 | 2026-06-09T20:07:14 | 1440 | 72 | 1*5*H400653
S63838 | Bulloch 1A | https://apps.alsoenergy.com/powertrack/S63838/analysis/ruletool |  | ruletool
S63839 | Richmond | https://apps.alsoenergy.com/powertrack/S63839/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S63839 | Richmond | https://apps.alsoenergy.com/powertrack/S63839/analysis/chartbuilder?c=79&start=2026-05-10T20:07:26&end=2026-06-09T20:07:26&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:07:26 | 2026-06-09T20:07:26 | 1440 | 79 | 2*5*11
S63839 | Richmond | https://apps.alsoenergy.com/powertrack/S63839/analysis/chartbuilder?c=259&start=2026-05-10T20:07:26&end=2026-06-09T20:07:26&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:07:26 | 2026-06-09T20:07:26 | 1440 | 259 | 1*5*11
S63839 | Richmond | https://apps.alsoenergy.com/powertrack/S63839/analysis/chartbuilder?c=206&start=2026-06-02T20:07:26&end=2026-06-09T20:07:26&bin=1440&h=24&p=%5b%7b%22id%22%3a59%2c%22value%22%3atrue%7d%2c%7b%22id%22%3a |  | chartbuilder | 2026-06-02T20:07:26 | 2026-06-09T20:07:26 | 1440 | 206 | 24
S63839 | Richmond | https://apps.alsoenergy.com/powertrack/S63839/analysis/ruletool |  | ruletool
S63840 | Upson | https://apps.alsoenergy.com/powertrack/S63840/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S63840 | Upson | https://apps.alsoenergy.com/powertrack/S63840/analysis/chartbuilder?c=79&start=2026-05-10T20:07:39&end=2026-06-09T20:07:39&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:07:39 | 2026-06-09T20:07:39 | 1440 | 79 | 2*5*11
S63840 | Upson | https://apps.alsoenergy.com/powertrack/S63840/analysis/chartbuilder?c=259&start=2026-05-10T20:07:39&end=2026-06-09T20:07:39&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:07:39 | 2026-06-09T20:07:39 | 1440 | 259 | 1*5*11
S63840 | Upson | https://apps.alsoenergy.com/powertrack/S63840/analysis/chartbuilder?c=72&start=2026-05-10T20:07:39&end=2026-06-09T20:07:39&bin=1440&h=1*5*H401052 |  | chartbuilder | 2026-05-10T20:07:39 | 2026-06-09T20:07:39 | 1440 | 72 | 1*5*H401052
S63840 | Upson | https://apps.alsoenergy.com/powertrack/S63840/analysis/ruletool |  | ruletool
S64602 | McLean | https://apps.alsoenergy.com/powertrack/S64602/analysis/chartbuilder?c=79&start=2026-05-10T20:07:53&end=2026-06-09T20:07:53&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:07:53 | 2026-06-09T20:07:53 | 1440 | 79 | 2*5*11
S64602 | McLean | https://apps.alsoenergy.com/powertrack/S64602/analysis/chartbuilder?c=259&start=2026-05-10T20:07:53&end=2026-06-09T20:07:53&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:07:53 | 2026-06-09T20:07:53 | 1440 | 259 | 1*5*11
S64602 | McLean | https://apps.alsoenergy.com/powertrack/S64602/analysis/chartbuilder?c=206&start=2026-06-02T20:07:53&end=2026-06-09T20:07:53&bin=1440&h=24 |  | chartbuilder | 2026-06-02T20:07:53 | 2026-06-09T20:07:53 | 1440 | 206 | 24
S64602 | McLean | https://apps.alsoenergy.com/powertrack/S64602/operations/alerts |  | alerts
S64602 | McLean | https://apps.alsoenergy.com/powertrack/S64602/analysis/ruletool |  | ruletool
S64603 | Shorthorn | https://apps.alsoenergy.com/powertrack/S64603/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S64603 | Shorthorn | https://apps.alsoenergy.com/powertrack/S64603/analysis/chartbuilder?c=79&start=2026-05-10T20:08:08&end=2026-06-09T20:08:08&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:08:08 | 2026-06-09T20:08:08 | 1440 | 79 | 2*5*11
S64603 | Shorthorn | https://apps.alsoenergy.com/powertrack/S64603/analysis/chartbuilder?c=79&start=2026-05-10T20:08:08&end=2026-06-09T20:08:08&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:08:08 | 2026-06-09T20:08:08 | 1440 | 79 | 2*5*11
S64603 | Shorthorn | https://apps.alsoenergy.com/powertrack/S64603/analysis/chartbuilder?c=259&start=2026-05-10T20:08:08&end=2026-06-09T20:08:08&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:08:08 | 2026-06-09T20:08:08 | 1440 | 259 | 1*5*11
S64603 | Shorthorn | https://apps.alsoenergy.com/powertrack/S64603/analysis/chartbuilder?c=206&start=2026-06-02T20:08:08&end=2026-06-09T20:08:08&bin=1440&h=24 |  | chartbuilder | 2026-06-02T20:08:08 | 2026-06-09T20:08:08 | 1440 | 206 | 24
S64603 | Shorthorn | https://apps.alsoenergy.com/powertrack/S64603/operations/alerts |  | alerts
S64603 | Shorthorn | https://apps.alsoenergy.com/powertrack/S64603/analysis/ruletool |  | ruletool
S65216 | Green Solar | https://apps.alsoenergy.com/powertrack/S65216/analysis/chartbuilder?c=6&start=2026-06-02T17:00:00&end=2026-06-09T17:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T17:00:00 | 2026-06-09T17:00:00 | 60 | 6 | 1*2*5*11
S65216 | Green Solar | https://apps.alsoenergy.com/powertrack/S65216/analysis/chartbuilder?c=79&start=2026-05-10T17:08:23&end=2026-06-09T17:08:23&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T17:08:23 | 2026-06-09T17:08:23 | 1440 | 79 | 2*5*11
S65216 | Green Solar | https://apps.alsoenergy.com/powertrack/S65216/analysis/chartbuilder?c=259&start=2026-05-10T17:08:23&end=2026-06-09T17:08:23&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T17:08:23 | 2026-06-09T17:08:23 | 1440 | 259 | 1*5*11
S65216 | Green Solar | https://apps.alsoenergy.com/powertrack/S65216/analysis/chartbuilder?c=72&start=2026-05-10T17:08:23&end=2026-06-09T17:08:23&bin=1440&h=1*5*H431106 |  | chartbuilder | 2026-05-10T17:08:23 | 2026-06-09T17:08:23 | 1440 | 72 | 1*5*H431106
S65216 | Green Solar | https://apps.alsoenergy.com/powertrack/S65216/analysis/ruletool |  | ruletool
S65784 | Washington Solar | https://apps.alsoenergy.com/powertrack/S65784/analysis/chartbuilder?c=259&start=2026-05-10T20:08:35&end=2026-06-09T20:08:35&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:08:35 | 2026-06-09T20:08:35 | 1440 | 259 | 1*5*11
S65784 | Washington Solar | https://apps.alsoenergy.com/powertrack/S65784/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S65784 | Washington Solar | https://apps.alsoenergy.com/powertrack/S65784/analysis/chartbuilder?c=79&start=2026-05-10T20:08:35&end=2026-06-09T20:08:35&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:08:35 | 2026-06-09T20:08:35 | 1440 | 79 | 2*5*11
S65784 | Washington Solar | https://apps.alsoenergy.com/powertrack/S65784/analysis/ruletool |  | ruletool
S65784 | Washington Solar | https://apps.alsoenergy.com/powertrack/S65784/analysis/chartbuilder?c=206&start=2026-06-02T20:08:35&end=2026-06-09T20:08:35&bin=1440&h=24 |  | chartbuilder | 2026-06-02T20:08:35 | 2026-06-09T20:08:35 | 1440 | 206 | 24
S65785 | Harding Solar | https://apps.alsoenergy.com/powertrack/S65785/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S65785 | Harding Solar | https://apps.alsoenergy.com/powertrack/S65785/analysis/chartbuilder?c=79&start=2026-05-10T20:08:50&end=2026-06-09T20:08:50&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:08:50 | 2026-06-09T20:08:50 | 1440 | 79 | 2*5*11
S65785 | Harding Solar | https://apps.alsoenergy.com/powertrack/S65785/analysis/chartbuilder?c=259&start=2026-05-10T20:08:50&end=2026-06-09T20:08:50&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:08:50 | 2026-06-09T20:08:50 | 1440 | 259 | 1*5*11
S65785 | Harding Solar | https://apps.alsoenergy.com/powertrack/S65785/analysis/chartbuilder?c=72&start=2026-05-10T20:08:50&end=2026-06-09T20:08:50&bin=1440&h=1*5*H462599 |  | chartbuilder | 2026-05-10T20:08:50 | 2026-06-09T20:08:50 | 1440 | 72 | 1*5*H462599
S65785 | Harding Solar | https://apps.alsoenergy.com/powertrack/S65785/analysis/ruletool |  | ruletool
S65785 | Harding Solar | https://apps.alsoenergy.com/powertrack/S65785/operations/alerts |  | alerts
S65786 | Whitehall Solar | https://apps.alsoenergy.com/powertrack/S65786/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S65786 | Whitehall Solar | https://apps.alsoenergy.com/powertrack/S65786/analysis/chartbuilder?c=79&start=2026-05-10T20:09:02&end=2026-06-09T20:09:02&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:09:02 | 2026-06-09T20:09:02 | 1440 | 79 | 2*5*11
S65786 | Whitehall Solar | https://apps.alsoenergy.com/powertrack/S65786/analysis/chartbuilder?c=259&start=2026-05-10T20:09:02&end=2026-06-09T20:09:02&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:09:02 | 2026-06-09T20:09:02 | 1440 | 259 | 1*5*11
S65786 | Whitehall Solar | https://apps.alsoenergy.com/powertrack/S65786/analysis/chartbuilder?c=72&start=2026-05-10T20:09:02&end=2026-06-09T20:09:02&bin=1440&h=1*5*H463299 |  | chartbuilder | 2026-05-10T20:09:02 | 2026-06-09T20:09:02 | 1440 | 72 | 1*5*H463299
S65786 | Whitehall Solar | https://apps.alsoenergy.com/powertrack/S65786/analysis/ruletool |  | ruletool
S65787 | Sunflower Solar | https://apps.alsoenergy.com/powertrack/S65787/analysis/chartbuilder?c=15&start=2026-05-10T20:09:14&end=2026-06-09T20:09:14&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:09:14 | 2026-06-09T20:09:14 | 1440 | 15 | 1*2*5*11
S65787 | Sunflower Solar | https://apps.alsoenergy.com/powertrack/S65787/analysis/chartbuilder?c=79&start=2026-05-10T20:09:14&end=2026-06-09T20:09:14&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:09:14 | 2026-06-09T20:09:14 | 1440 | 79 | 2*5*11
S65787 | Sunflower Solar | https://apps.alsoenergy.com/powertrack/S65787/analysis/chartbuilder?c=259&start=2026-05-10T20:09:14&end=2026-06-09T20:09:14&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:09:14 | 2026-06-09T20:09:14 | 1440 | 259 | 1*5*11
S65787 | Sunflower Solar | https://apps.alsoenergy.com/powertrack/S65787/analysis/ruletool |  | ruletool
S65788 | Gray Fox Solar | https://apps.alsoenergy.com/powertrack/S65788/analysis/chartbuilder?c=79&start=2026-05-10T20:09:31&end=2026-06-09T20:09:31&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:09:31 | 2026-06-09T20:09:31 | 1440 | 79 | 2*5*11
S65788 | Gray Fox Solar | https://apps.alsoenergy.com/powertrack/S65788/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S65788 | Gray Fox Solar | https://apps.alsoenergy.com/powertrack/S65788/analysis/chartbuilder?c=79&start=2026-05-10T20:09:31&end=2026-06-09T20:09:31&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:09:31 | 2026-06-09T20:09:31 | 1440 | 79 | 2*5*11
S65788 | Gray Fox Solar | https://apps.alsoenergy.com/powertrack/S65788/analysis/chartbuilder?c=259&start=2026-05-10T20:09:31&end=2026-06-09T20:09:31&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:09:31 | 2026-06-09T20:09:31 | 1440 | 259 | 1*5*11
S65788 | Gray Fox Solar | https://apps.alsoenergy.com/powertrack/S65788/operations/alerts |  | alerts
S65918 | C & B Graham Energy | https://apps.alsoenergy.com/powertrack/S65918/analysis/chartbuilder?c=15&start=2026-05-10T20:09:44&end=2026-06-09T20:09:44&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:09:44 | 2026-06-09T20:09:44 | 1440 | 15 | 1*2*5*11
S65918 | C & B Graham Energy | https://apps.alsoenergy.com/powertrack/S65918/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S65918 | C & B Graham Energy | https://apps.alsoenergy.com/powertrack/S65918/analysis/chartbuilder?c=79&start=2026-05-10T20:09:44&end=2026-06-09T20:09:44&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:09:44 | 2026-06-09T20:09:44 | 1440 | 79 | 2*5*11
S65918 | C & B Graham Energy | https://apps.alsoenergy.com/powertrack/S65918/operations/alerts |  | alerts
S66000 | Auburn Solar | https://apps.alsoenergy.com/powertrack/S66000/analysis/chartbuilder?c=6&start=2026-06-02T17:00:00&end=2026-06-09T17:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T17:00:00 | 2026-06-09T17:00:00 | 60 | 6 | 1*2*5*11
S66000 | Auburn Solar | https://apps.alsoenergy.com/powertrack/S66000/analysis/chartbuilder?c=79&start=2026-05-10T17:09:58&end=2026-06-09T17:09:58&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T17:09:58 | 2026-06-09T17:09:58 | 1440 | 79 | 2*5*11
S66000 | Auburn Solar | https://apps.alsoenergy.com/powertrack/S66000/analysis/chartbuilder?c=259&start=2026-05-10T17:09:58&end=2026-06-09T17:09:58&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T17:09:58 | 2026-06-09T17:09:58 | 1440 | 259 | 1*5*11
S66000 | Auburn Solar | https://apps.alsoenergy.com/powertrack/S66000/analysis/chartbuilder?c=206&start=2026-06-02T17:09:58&end=2026-06-09T17:09:58&bin=1440&h=24 |  | chartbuilder | 2026-06-02T17:09:58 | 2026-06-09T17:09:58 | 1440 | 206 | 24
S66001 | Sheridan Solar | https://apps.alsoenergy.com/powertrack/S66001/analysis/chartbuilder?c=79&start=2026-05-10T17:10:09&end=2026-06-09T17:10:09&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T17:10:09 | 2026-06-09T17:10:09 | 1440 | 79 | 2*5*11
S66001 | Sheridan Solar | https://apps.alsoenergy.com/powertrack/S66001/analysis/chartbuilder?c=259&start=2026-05-10T17:10:09&end=2026-06-09T17:10:09&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T17:10:09 | 2026-06-09T17:10:09 | 1440 | 259 | 1*5*11
S66001 | Sheridan Solar | https://apps.alsoenergy.com/powertrack/S66001/analysis/chartbuilder?c=15&start=2026-05-10T17:10:09&end=2026-06-09T17:10:09&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T17:10:09 | 2026-06-09T17:10:09 | 1440 | 15 | 1*2*5*11
S66001 | Sheridan Solar | https://apps.alsoenergy.com/powertrack/S66001/analysis/ruletool |  | ruletool
S66930 | Elk Solar | https://apps.alsoenergy.com/powertrack/S66930/analysis/chartbuilder?c=72&start=2026-05-10T20:10:18&end=2026-06-09T20:10:18&bin=1440&h=1*5*H499741 |  | chartbuilder | 2026-05-10T20:10:18 | 2026-06-09T20:10:18 | 1440 | 72 | 1*5*H499741
S66930 | Elk Solar | https://apps.alsoenergy.com/powertrack/S66930/analysis/chartbuilder?c=259&start=2026-05-10T20:10:18&end=2026-06-09T20:10:18&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:10:18 | 2026-06-09T20:10:18 | 1440 | 259 | 1*5*11
S66930 | Elk Solar | https://apps.alsoenergy.com/powertrack/S66930/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S66930 | Elk Solar | https://apps.alsoenergy.com/powertrack/S66930/analysis/chartbuilder?c=259&start=2026-05-10T20:10:18&end=2026-06-09T20:10:18&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:10:18 | 2026-06-09T20:10:18 | 1440 | 259 | 1*5*11
S66930 | Elk Solar | https://apps.alsoenergy.com/powertrack/S66930/analysis/chartbuilder?c=15&start=2026-05-10T20:10:18&end=2026-06-09T20:10:18&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:10:18 | 2026-06-09T20:10:18 | 1440 | 15 | 1*2*5*11
S66930 | Elk Solar | https://apps.alsoenergy.com/powertrack/S66930/analysis/ruletool |  | ruletool
S68112 | Wallace Solar | https://apps.alsoenergy.com/powertrack/S68112/operations/alerts |  | alerts
S68112 | Wallace Solar | https://apps.alsoenergy.com/powertrack/S68112/analysis/chartbuilder?c=6&start=2026-06-02T17:00:00&end=2026-06-09T17:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T17:00:00 | 2026-06-09T17:00:00 | 60 | 6 | 1*2*5*11
S68112 | Wallace Solar | https://apps.alsoenergy.com/powertrack/S68112/analysis/chartbuilder?c=259&start=2026-05-10T17:10:34&end=2026-06-09T17:10:34&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T17:10:34 | 2026-06-09T17:10:34 | 1440 | 259 | 1*5*11
S68112 | Wallace Solar | https://apps.alsoenergy.com/powertrack/S68112/analysis/chartbuilder?c=79&start=2026-05-10T17:10:34&end=2026-06-09T17:10:34&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T17:10:34 | 2026-06-09T17:10:34 | 1440 | 79 | 2*5*11
S68112 | Wallace Solar | https://apps.alsoenergy.com/powertrack/S68112/analysis/ruletool |  | ruletool
S68113 | Marble Solar | https://apps.alsoenergy.com/powertrack/S68113/analysis/chartbuilder?c=79&start=2026-05-10T17:10:44&end=2026-06-09T17:10:44&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T17:10:44 | 2026-06-09T17:10:44 | 1440 | 79 | 2*5*11
S68113 | Marble Solar | https://apps.alsoenergy.com/powertrack/S68113/analysis/chartbuilder?c=259&start=2026-05-10T17:10:44&end=2026-06-09T17:10:44&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T17:10:44 | 2026-06-09T17:10:44 | 1440 | 259 | 1*5*11
S68113 | Marble Solar | https://apps.alsoenergy.com/powertrack/S68113/analysis/chartbuilder?c=15&start=2026-05-10T17:10:44&end=2026-06-09T17:10:44&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T17:10:44 | 2026-06-09T17:10:44 | 1440 | 15 | 1*2*5*11
S68113 | Marble Solar | https://apps.alsoenergy.com/powertrack/S68113/analysis/chartbuilder?c=72&start=2026-05-10T17:10:44&end=2026-06-09T17:10:44&bin=1440&h=1*5*H503496 |  | chartbuilder | 2026-05-10T17:10:44 | 2026-06-09T17:10:44 | 1440 | 72 | 1*5*H503496
S68113 | Marble Solar | https://apps.alsoenergy.com/powertrack/S68113/analysis/chartbuilder?c=206&start=2026-06-02T17:10:44&end=2026-06-09T17:10:44&bin=1440&h=24&p=%5b%7b%22id%22%3a59%2c%22value%22%3atrue%7d%2c%7b%22id%22%3a |  | chartbuilder | 2026-06-02T17:10:44 | 2026-06-09T17:10:44 | 1440 | 206 | 24
S70532 | Longleaf Pine Solar, LLC | https://apps.alsoenergy.com/powertrack/S70532/analysis/chartbuilder?c=6&start=2026-06-02T20:00:00&end=2026-06-09T20:00:00&bin=60&h=1*2*5*11 |  | chartbuilder | 2026-06-02T20:00:00 | 2026-06-09T20:00:00 | 60 | 6 | 1*2*5*11
S70532 | Longleaf Pine Solar, LLC | https://apps.alsoenergy.com/powertrack/S70532/analysis/chartbuilder?c=15&start=2026-05-10T20:10:54&end=2026-06-09T20:10:54&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:10:54 | 2026-06-09T20:10:54 | 1440 | 15 | 1*2*5*11
S70532 | Longleaf Pine Solar, LLC | https://apps.alsoenergy.com/powertrack/S70532/analysis/chartbuilder?c=79&start=2026-05-10T20:10:54&end=2026-06-09T20:10:54&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:10:54 | 2026-06-09T20:10:54 | 1440 | 79 | 2*5*11
S70532 | Longleaf Pine Solar, LLC | https://apps.alsoenergy.com/powertrack/S70532/analysis/chartbuilder?c=259&start=2026-05-10T20:10:54&end=2026-06-09T20:10:54&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:10:54 | 2026-06-09T20:10:54 | 1440 | 259 | 1*5*11
S70532 | Longleaf Pine Solar, LLC | https://apps.alsoenergy.com/powertrack/S70532/operations/alerts |  | alerts
S70645 | Williams Solar, LLC | https://apps.alsoenergy.com/powertrack/S70645/analysis/chartbuilder?c=15&start=2026-05-10T20:11:09&end=2026-06-09T20:11:09&bin=1440&h=1*2*5*11 |  | chartbuilder | 2026-05-10T20:11:09 | 2026-06-09T20:11:09 | 1440 | 15 | 1*2*5*11
S70645 | Williams Solar, LLC | https://apps.alsoenergy.com/powertrack/S70645/operations/alerts |  | alerts
S70645 | Williams Solar, LLC | https://apps.alsoenergy.com/powertrack/S70645/analysis/chartbuilder?c=72&start=2026-05-10T20:11:09&end=2026-06-09T20:11:09&bin=1440&h=1*5*H543196 |  | chartbuilder | 2026-05-10T20:11:09 | 2026-06-09T20:11:09 | 1440 | 72 | 1*5*H543196
S70645 | Williams Solar, LLC | https://apps.alsoenergy.com/powertrack/S70645/analysis/chartbuilder?c=79&start=2026-05-10T20:11:09&end=2026-06-09T20:11:09&bin=1440&h=2*5*11 |  | chartbuilder | 2026-05-10T20:11:09 | 2026-06-09T20:11:09 | 1440 | 79 | 2*5*11
S70645 | Williams Solar, LLC | https://apps.alsoenergy.com/powertrack/S70645/analysis/chartbuilder?c=259&start=2026-05-10T20:11:09&end=2026-06-09T20:11:09&bin=1440&h=1*5*11 |  | chartbuilder | 2026-05-10T20:11:09 | 2026-06-09T20:11:09 | 1440 | 259 | 1*5*11
S55935 | Manuel Lawrence Dairy | https://apps.alsoenergy.com/powertrack/S55935/analysis/ruletool |  | ruletool

## Device Mentions
site_key | site_name | device
S40834 | Green Elementary | meters
S40834 | Green Elementary | Meter-to-inverter ratio is 0.97
S40834 | Green Elementary | gateway are communicating as of Jun 9 at 8
S40834 | Green Elementary | weather stations
S40834 | Green Elementary | inverter losses
S40834 | Green Elementary | inverter availability
S40834 | Green Elementary | inverters
S40835 | Gallia Academy | meter alert
S40835 | Gallia Academy | meter as of today â
S40835 | Gallia Academy | Inverter 12 shows
S40835 | Gallia Academy | inverters are producing today
S40835 | Gallia Academy | inverters not producing
S40835 | Gallia Academy | inverter
S40835 | Gallia Academy | Meter-to-inverter ratio today is
S40835 | Gallia Academy | Inverter - 1 has been offline since Apr 6 at 10
S40835 | Gallia Academy | inverter. Meter-to-inverter ratio is 0.97
S40835 | Gallia Academy | Inverter - 1
S40836 | Rio Grande Elementary | Weather Station 2
S40836 | Rio Grande Elementary | Meter-to-inverter ratio is 0.97
S40836 | Rio Grande Elementary | meter
S40836 | Rio Grande Elementary | inverters online and producing as of Jun 9 at 8
S40836 | Rio Grande Elementary | sensor needs attention but does not affect expected energy
S40836 | Rio Grande Elementary | inverter
S40836 | Rio Grande Elementary | Weather Station 1 drives the model
S40836 | Rio Grande Elementary | inverter availability
S44485 | RRH 1 & 2 | inverter PV model losses show no notable issues beyond normal age and inverter losses. Meter-to-inverter ratio is 1.00
S44485 | RRH 1 & 2 | sensor calibration drift worth review.
S44485 | RRH 1 & 2 | inverters. Forecast is light rain through Jun 12 with highs 73â
S44485 | RRH 1 & 2 | inverters online and producing normally as of Jun 9 at 8
S44485 | RRH 1 & 2 | Inverter availability
S44485 | RRH 1 & 2 | Meters Site 1 and Site 2
S44566 | RIT | Meter-to-inverter ratio is 0.99
S44566 | RIT | sensor calibration issue worth review
S44566 | RIT | inverters are online and producing as of Jun 9 at 8
S44566 | RIT | inverter
S44566 | RIT | inverters and low diffuse shade factor configuration warnings. Forecast is light rain with highs 77â
S44566 | RIT | inverter availability is 94
S44882 | Monroe Landfill | inverters suggest a PV model or weather station calibration issue. Meter-to-inverter ratio is 0.99
S44882 | Monroe Landfill | inverters are online and producing in line with peers as of Jun 9 at 8
S44882 | Monroe Landfill | inverter availability is 96
S44882 | Monroe Landfill | inverter
S44882 | Monroe Landfill | Inverter 20 has been offline since May 30
S44882 | Monroe Landfill | meter. Currently clear
S51957 | WCPS - William Perry Elementary School | inverters are online and producing as of Jun 9 at 7
S51957 | WCPS - William Perry Elementary School | inverters per the
S51957 | WCPS - William Perry Elementary School | Meter-to-inverter ratio is 1.00
S51957 | WCPS - William Perry Elementary School | inverter availability at 100
S51957 | WCPS - William Perry Elementary School | Inverter-1
S51957 | WCPS - William Perry Elementary School | inverter PV model losses
S51957 | WCPS - William Perry Elementary School | meter and weather station reporting normally. Today
S51958 | WCPS - Westwood Hills Elementary School | meter
S51958 | WCPS - Westwood Hills Elementary School | inverters are online and producing as of Jun 9 at 6
S51958 | WCPS - Westwood Hills Elementary School | Meter-to-inverter ratio is 1.00
S51958 | WCPS - Westwood Hills Elementary School | inverter
S51958 | WCPS - Westwood Hills Elementary School | inverter availability
S51958 | WCPS - Westwood Hills Elementary School | Modem â
S51959 | WCPS - Waynesboro High School | inverters are online and producing as of Jun 9 at 7
S51959 | WCPS - Waynesboro High School | inverter show
S51959 | WCPS - Waynesboro High School | weather station calibration issue
S51959 | WCPS - Waynesboro High School | meter-to-inverter ratio is 1.00
S51959 | WCPS - Waynesboro High School | inverter availability
S51960 | WCPS - Kate Collins Middle School | Meter-to-inverter ratio is 0.99
S51960 | WCPS - Kate Collins Middle School | inverters online and producing as of Jun 9 at 6
S51960 | WCPS - Kate Collins Middle School | Inverter 1 across every daylight hour
S51960 | WCPS - Kate Collins Middle School | inverter availability at 100
S51960 | WCPS - Kate Collins Middle School | Inverters 2 and 3 consistently produce
S51960 | WCPS - Kate Collins Middle School | Inverter 1
S51960 | WCPS - Kate Collins Middle School | combiner
S54553 | Butler Maple | Meter-to-inverter ratio is 0.99
S54553 | Butler Maple | Relay default alerts not enabled â
S54553 | Butler Maple | Tracker losses
S54553 | Butler Maple | inverter PV model losses
S54553 | Butler Maple | sensor calibration and relay alert configuration. Forecast calls for light rain Jun 10
S54553 | Butler Maple | inverter availability
S54553 | Butler Maple | Inverter-1 is producing normally
S54613 | Warbler | inverter availability
S54613 | Warbler | inverters are online and communicating as of Jun 9 at 8
S54613 | Warbler | Meter-to-inverter ratio 0.99
S54613 | Warbler | inverter
S54681 | Eagle | inverters are online and producing in line with peers as of Jun 9 at 8
S54681 | Eagle | inverter. Meter-to-inverter ratio is 0.99 â
S59656 | Whitetail | tracker energy loss observed
S59656 | Whitetail | Tracker Control 2.1 E-Stop
S59656 | Whitetail | Tracker Control remains stale.
S59656 | Whitetail | tracker lost energy is 0 kWh over 7 days. Meter-to-inverter ratio is 0.99
S59656 | Whitetail | inverters online and reporting as of Jun 9 at 8
S59656 | Whitetail | inverter
S59656 | Whitetail | inverters 22
S59656 | Whitetail | sensor tilt
S59656 | Whitetail | inverter availability 99
S63837 | Bulloch 1B | inverter show no major issues
S63837 | Bulloch 1B | inverter availability at 100
S63837 | Bulloch 1B | inverters online and reporting as of Jun 9 at 8
S63837 | Bulloch 1B | Meter-to-inverter ratio is 0.98
S63837 | Bulloch 1B | tracker lost energy
S63837 | Bulloch 1B | trackers stuck at fixed angles
S63838 | Bulloch 1A | inverters online and reporting fresh telemetry as of Jun 9 at 8
S63838 | Bulloch 1A | Tracker losses remain small
S63838 | Bulloch 1A | UPS default alerts not set â
S63838 | Bulloch 1A | inverter
S63838 | Bulloch 1A | Tracker
S63838 | Bulloch 1A | Meter-to-inverter ratio is 0.98
S63838 | Bulloch 1A | inverter availability
S63839 | Richmond | trackers stuck
S63839 | Richmond | tracker losses
S63839 | Richmond | inverters online and producing as of Jun 9 at 8
S63839 | Richmond | Meter-to-inverter ratio is 0.98
S63839 | Richmond | inverter PV model losses show no notable findings
S63839 | Richmond | inverter availability
S63839 | Richmond | inverter-group configuration items
S63839 | Richmond | tracker losses. Forecast
S63840 | Upson | sensor calibration
S63840 | Upson | sensors
S63840 | Upson | UPS default alerts unset
S63840 | Upson | Meter-to-inverter ratio is 0.98 over 30 days â
S63840 | Upson | pyranometer and low BPOA insolation â
S63840 | Upson | meter PF near zero noted. Forecast is clear with highs 88â
S63840 | Upson | inverter availability at 100
S63840 | Upson | inverters online and reporting as of Jun 9 at 8
S63840 | Upson | inverter
S63840 | Upson | tracker losses are under 1 kWh
S64602 | McLean | inverters communicating as of Jun 9 at 8
S64602 | McLean | tracker positions reading 0Â
S64602 | McLean | tracker slave SOC alarms
S64602 | McLean | tracker rows. Meter-to-inverter ratio is 0.98
S64602 | McLean | inverter
S64602 | McLean | PYRANOMETER - BPOA
S64602 | McLean | inverter availability
S64602 | McLean | tracker lost energy
S64603 | Shorthorn | trackers with elevated position error or stuck at 0Â
S64603 | Shorthorn | inverters communicating as of Jun 9 at 8
S64603 | Shorthorn | tracker losses
S64603 | Shorthorn | meter current mismatch alert
S64603 | Shorthorn | inverter losses and
S64603 | Shorthorn | inverter availability at 99
S64603 | Shorthorn | Meter-to-inverter ratio is 0.98
S64603 | Shorthorn | tracker alerts
S65216 | Green Solar | inverter availability at 99
S65216 | Green Solar | tracker losses. Meter-to-inverter ratio is 0.99
S65216 | Green Solar | Inverter 1 is online and producing
S65216 | Green Solar | inverter
S65784 | Washington Solar | inverters communicating as of Jun 9 at 8
S65784 | Washington Solar | tracker losses
S65784 | Washington Solar | inverters and many trackers stuck at 0Â
S65784 | Washington Solar | INVERTER 6 invalid-data warning that triggered at 8
S65784 | Washington Solar | Meter-to-inverter ratio is 0.98
S65784 | Washington Solar | sensor calibration issue worth review. 30-day production is 1
S65785 | Harding Solar | UPS Battery Over Temperature alert
S65785 | Harding Solar | tracker losses
S65785 | Harding Solar | Inverters 3
S65785 | Harding Solar | UPS continues reporting. Forecast
S65785 | Harding Solar | inverters online and producing normally as of Jun 9 at 8
S65785 | Harding Solar | tracker position error of
S65785 | Harding Solar | inverter
S65785 | Harding Solar | Meter-to-inverter ratio is 0.98
S65785 | Harding Solar | inverter availability
S65786 | Whitehall Solar | sensor calibration
S65786 | Whitehall Solar | inverter derating but no stow risk with light winds.
S65786 | Whitehall Solar | inverters online and producing as of Jun 9 at 8
S65786 | Whitehall Solar | weather station module-temp sensor reading below ambient â
S65786 | Whitehall Solar | tracker losses are negligible
S65786 | Whitehall Solar | inverter
S65786 | Whitehall Solar | inverter availability
S65786 | Whitehall Solar | Meter-to-inverter ratio is 0.98
S65787 | Sunflower Solar | inverters are communicating and operating as of Jun 9 at 8
S65787 | Sunflower Solar | sensor and tracker alignment. Forecast is light rain with highs 93â
S65787 | Sunflower Solar | meter
S65787 | Sunflower Solar | weather station
S65787 | Sunflower Solar | tracker-error and POA insolation-mismatch flags
S65787 | Sunflower Solar | tracker losses are minor
S65787 | Sunflower Solar | inverter
S65787 | Sunflower Solar | trackers reporting normally. Light rain is on site at 79Â
S65787 | Sunflower Solar | Meter-to-inverter ratio is 0.98
S65787 | Sunflower Solar | inverter availability is 99
S65788 | Gray Fox Solar | inverters communicating as of Jun 9 at 8
S65788 | Gray Fox Solar | inverter availability 97
S65788 | Gray Fox Solar | inverter and tracker losses show nothing notable. Meter-to-inverter ratio is 0.98
S65918 | C & B Graham Energy | metering data gap. Multiple
S65918 | C & B Graham Energy | inverters are confirmed offline based on
S65918 | C & B Graham Energy | weather station offline. Forecast
S65918 | C & B Graham Energy | meter-to-inverter ratio on reporting meters
S65918 | C & B Graham Energy | meter shows 22
S65918 | C & B Graham Energy | METER 2 and METER 3
S65918 | C & B Graham Energy | inverter outages and rainy periods
S65918 | C & B Graham Energy | pyranometer
S65918 | C & B Graham Energy | weather station data issues. METER 1 not reporting since Apr 27
S66000 | Auburn Solar | pyranometer calibration drift worth reviewing.
S66000 | Auburn Solar | meter configuration. No active alerts and rule tool is clean. Forecast
S66000 | Auburn Solar | Inverter 1 producing normally through the afternoon under light rain conditions. Today
S66000 | Auburn Solar | Tracker losses
S66000 | Auburn Solar | Meter-to-inverter ratio is 1.01
S66000 | Auburn Solar | inverter availability is 100
S66001 | Sheridan Solar | Meter-to-inverter ratio is 0.99
S66001 | Sheridan Solar | tracker losses are minimal
S66001 | Sheridan Solar | weather station temperature â
S66001 | Sheridan Solar | Inverter 1 is online and producing
S66001 | Sheridan Solar | sensor calibration but no production impact. Forecast
S66001 | Sheridan Solar | inverter
S66001 | Sheridan Solar | inverter availability
S66930 | Elk Solar | tracker losses
S66930 | Elk Solar | metering issue.
S66930 | Elk Solar | meter
S66930 | Elk Solar | Inverter 01.15 also shows zero production with stuck AC telemetry â
S66930 | Elk Solar | Inverters 01.01 and 01.05 show low energy ratios
S66930 | Elk Solar | inverter availability 95
S66930 | Elk Solar | trackers and abnormal motor currents
S66930 | Elk Solar | Inverter 01.02 has been offline since May 27 at 3
S66930 | Elk Solar | inverter
S66930 | Elk Solar | inverter outage represents
S68112 | Wallace Solar | Tracker losses were minimal
S68112 | Wallace Solar | Meter-to-inverter ratio is 0.99
S68112 | Wallace Solar | Inverter availability
S68112 | Wallace Solar | Inverter 1 is online and producing
S68112 | Wallace Solar | pyranometer azimuth
S68112 | Wallace Solar | sensors and low BPOA â
S68113 | Marble Solar | tracker losses
S68113 | Marble Solar | Meter-to-inverter ratio is 0.99
S68113 | Marble Solar | Inverter 1 produced about 2.6 MW peak earlier today under clear skies and 61Â
S68113 | Marble Solar | inverter availability at 100
S68113 | Marble Solar | inverter
S70532 | Longleaf Pine Solar, LLC | Tracker Controller 1 has been offline since Jun 3 with minimal energy impact
S70532 | Longleaf Pine Solar, LLC | tracker error per
S70532 | Longleaf Pine Solar, LLC | meter chart
S70532 | Longleaf Pine Solar, LLC | meter and inverter production both days visible on the
S70532 | Longleaf Pine Solar, LLC | inverters are online and producing as of Jun 9 at 8
S70532 | Longleaf Pine Solar, LLC | Meter-to-inverter ratio is 0.98
S70532 | Longleaf Pine Solar, LLC | inverter availability
S70645 | Williams Solar, LLC | inverters are online and producing normally under clear skies. INVERTER A20 forced outage
S70645 | Williams Solar, LLC | inverter
S70645 | Williams Solar, LLC | meter-to-inverter ratio
S70645 | Williams Solar, LLC | INVERTER A20 has been offline since Jun 5 with zero production while peers operate normally. The
S70645 | Williams Solar, LLC | inverter availability
S70645 | Williams Solar, LLC | Tracker losses minimal
S55935 | Manuel Lawrence Dairy | Inverter derating is possible during peak afternoon hours later this week. Data retrieval should be restored to enable proper performance assessment.
S55935 | Manuel Lawrence Dairy | tracker. These findings cannot be validated against meter-to-inverter ratio or production charts due to the data retrieval failures noted above. Forecast is clear and hot through Jun 12
S55935 | Manuel Lawrence Dairy | inverter availability and is unable to calculate PV losses across all 15 CPS SCA 60KTL-DO inverters or energy ratio at the Elkor production meter. The IMT reference cell is also reporting invalid module temperature and irradiance

## Action Items
site_key | site_name | action
S40836 | Rio Grande Elementary | Meter-to-inverter ratio is 0.97, normal. [Rule tool](https://apps.alsoenergy.com/powertrack/S40836/analysis/ruletool) flags Weather Station 2 (GHI) module temperature stuck at -40Â°F â sensor needs
S51960 | WCPS - Kate Collins Middle School | Inverters 2 and 3 consistently produce ~30â35% less than Inverter 1 across every daylight hour, flagged by the [rule tool](https://apps.alsoenergy.com/powertrack/S51960/analysis/ruletool) as low ene
S64602 | McLean | Meter-to-inverter ratio is 0.98, normal. Monitoring flags: [PYRANOMETER - BPOA (PY2) offline since Jun 16, 2025](https://apps.alsoenergy.com/powertrack/S64602/operations/alerts) (equipment repair need
S66930 | Elk Solar | 30-day [inverter availability 95%](https://apps.alsoenergy.com/powertrack/S66930/analysis/chartbuilder?c=259&start=2026-05-10T20:10:18&end=2026-06-09T20:10:18&bin=1440&h=1*5*11); actual/expected 90%.
S68112 | Wallace Solar | Meter-to-inverter ratio is 0.99, normal. The [rule tool](https://apps.alsoenergy.com/powertrack/S68112/analysis/ruletool) flags POA insolation +55% higher than other sensors and low BPOA â consisten
S55935 | Manuel Lawrence Dairy | Forecast is clear and hot through Jun 12, with highs reaching 109Â°F. Inverter derating is possible during peak afternoon hours later this week. Data retrieval should be restored to enable proper perf

## Full Summaries
Site Key | Site Name | Full Summary Text
S40834 | Green Elementary | All 11 Solectria PVI 28TL inverters, both meters, weather stations, and the gateway are communicating as of Jun 9 at 8:02 PM EDT. Today's production was limited by light rain, with peak hourly output near midday around 200 kWh site-wide. Over the last 30 days, the site averaged an Energy Performance Index of 0.88 with 100% inverter availability. 30-day production reached 92% of estimate. Sampled inverter losses show DC/AC age losses near 5% each and residual loss around 7%, consistent with a maturing system. Meter-to-inverter ratio is 0.97, which is normal. One stale Info-level rule tool alert from Jul 2025 remains open with no production correlation. Forecast calls for rain and light rain Jun 10â12 with highs 82â88Â°F; expect continued weather-limited output.
S40835 | Gallia Academy | Solectria Inverter - 1 has been offline since Apr 6 at 10:57 AM EDT, last upload confirms ~64 days down. Meter-to-inverter ratio today is ~1.06 â consistent with 1 of 20 inverters not producing, confirming an outage rather than comm loss. The remaining 19 inverters are producing today, with site output tracking expected energy under light rain (73Â°F). Inverter 12 shows ~29% residual loss versus peers â a persistent underperformance worth field review. Estimated loss from Inverter - 1: ~12 MWh over 64 days (~5% capacity, ~200 kWh/day per PV model losses for the sampled inverter). 30-day EPI averages 0.92; availability holds at 95%, reflecting the single offline inverter. Meter-to-inverter ratio is 0.97 (30-day) â normal. An active production meter alert flags a current mismatch (A/B/C phases) on the Main Elkor meter as of today â monitoring flag for CT/wiring review. Forecast: rain and light rain through Jun 12, highs 82â88Â°F. Expect reduced output on heavy-rain hours.
S40836 | Rio Grande Elementary | All 13 Solectria 28kW inverters online and producing as of Jun 9 at 8:02 PM EDT, with the site in light rain and near sunset. Recent production tracks reduced expected output under cloudy conditions, with no outages observed. 30-day Energy Performance Index averages 0.88 and inverter availability is 100%. Site produced 53.0 MWh against 58.1 MWh estimate (91%) per the production meter. Sampled-inverter PV model losses show DC/AC age (~5% each) and ~10% residual; no major events identified. Meter-to-inverter ratio is 0.97, normal. Rule tool flags Weather Station 2 (GHI) module temperature stuck at -40Â°F â sensor needs attention but does not affect expected energy (Weather Station 1 drives the model). Forecast calls for light rain and highs of 82â86Â°F through Jun 12; expect continued reduced output under cloud cover.
S44485 | RRH 1 & 2 | All 66 inverters online and producing normally as of Jun 9 at 8:04 PM EDT, with site output tracking expected through the day on production vs. expected. Current conditions are light rain at 70Â°F. 30-day Energy Performance Index averages 1.05, with several days in the 1.11â1.16 range suggesting possible PV model or POA sensor calibration drift worth review. Inverter availability is 100%. Sampled-inverter PV model losses show no notable issues beyond normal age and inverter losses. Meter-to-inverter ratio is 1.00, normal. Two active warnings flag current mismatch on Elkor Production Meters Site 1 and Site 2 (started Jun 9 at 7:41 PM and 7:44 PM); worth monitoring for CT or wiring issue though totals remain consistent with inverters. Forecast is light rain through Jun 12 with highs 73â81Â°F, expect reduced but normal production.
S44566 | RIT | All 27 inverters are online and producing as of Jun 9 at 8:04 PM EDT, with light rain and 72Â°F at site. Today's peak hourly output reached ~1.6 MW around midday, consistent with overcast conditions. The site is healthy. 30-day EPI averages ~1.10, and inverter availability is 94%, pulled down by reduced availability May 27â29 that has since fully recovered. 30-day production totaled 320 MWh vs. 334 MWh estimate (96%). Meter-to-inverter ratio is 0.99, normal. The persistently elevated EPI (~1.10) and large negative residual loss on the sampled inverter suggest a PV model or POA sensor calibration issue worth review, echoed by the rule tool's high energy ratio flags on 19 inverters and low diffuse shade factor configuration warnings. Forecast is light rain with highs 77â82Â°F through Jun 12 â reduced but normal production expected, no equipment risk.
S44882 | Monroe Landfill | Inverter 20 has been offline since May 30, confirmed by an Insulation Resistance Low (IsolationErr) fault and stuck-at-zero AC telemetry. Classified as a forced outage affecting ~73 kW (~3.7% of site capacity), with ~2.3 MWh lost over 11 days (~210 kWh/day expected per the PV model losses for the sampled inverter). All other 26 inverters are online and producing in line with peers as of Jun 9 at 8:03 PM EDT. 30-day EPI averages 1.18 and inverter availability is 96%, the latter dragged by INV-20. Sustained EPI above 1.1 and rule tool high-energy-ratio flags across all inverters suggest a PV model or weather station calibration issue. Meter-to-inverter ratio is 0.99 (normal). Default alerts not set on the Elkor meter. Currently clear, 72Â°F. Light rain forecast Jun 10â11, rain Jun 12; modest production reductions expected.
S51957 | WCPS - William Perry Elementary School | All three CPS SCA60KTL inverters are online and producing as of Jun 9 at 7:38 PM EDT, with the production meter and weather station reporting normally. Today's peak hourly output was modest (~130 kW combined around midday) under variable rain conditions, consistent with the Light rain currently at the site. The site has been underperforming throughout the 30-day window. The Energy Performance Index averages roughly 0.41, with inverter availability at 100% and 30-day production of 29,929 kWh vs. 35,102 kWh estimate (85%). Sampled inverter PV model losses show large DC/AC age losses (~83-88%) and 58% residual loss on Inverter-1, with similar residual losses across all three inverters per the rule tool. This persistent underperformance pattern warrants review. Meter-to-inverter ratio is 1.00 (normal). The Performance Index alert from May 24 reflects this ongoing underperformance. Forecast calls for light rain and warming highs into the low 90s through Jun 12, limiting production.
S51958 | WCPS - Westwood Hills Elementary School | All three inverters are online and producing as of Jun 9 at 6:00 PM EDT, with the production meter at 769.8 kWh today under light rain. Hardware is communicating normally. Current conditions (72Â°F, light rain) are consistent with the reduced afternoon output seen today. No production events occurred in the reporting window. The 30-day Energy Performance Index averaged 0.95 and inverter availability was 100%. Sampled-inverter PV model losses show routine AC/DC age (~3% each) and minor soiling (~1%); no major losses identified. Meter-to-inverter ratio is 1.00, which is normal. The rule tool flagged default-alert configuration items on the Microhard Modem â monitoring-only, no production impact. Forecast calls for light rain and highs of 82â91Â°F through Jun 12; expect continued weather-driven variability with no equipment risk.
S51959 | WCPS - Waynesboro High School | Both inverters are online and producing as of Jun 9 at 7:07 PM EDT, with the site generating 590 kWh today under light rain and overcast conditions. Today's peak hourly output reached ~97 kW around 2:00 PM, consistent with the cloudy weather. Over the last 30 days, the Energy Performance Index averaged 0.84 and inverter availability held at 100%. Production totaled 18.4 MWh, or 90% of the estimate. PV model losses for the sampled inverter show ~4% soiling and a large negative residual, suggesting the PV model may be over-predicting. The meter-to-inverter ratio is 1.00, normal. An informational EPI alert (index 1.32) triggered Jun 9 at 3:21 PM flags a possible weather station calibration issue, consistent with the negative residual losses. Light rain is forecast through Jun 12 with highs reaching 91Â°F, expect continued weather-driven variability.
S51960 | WCPS - Kate Collins Middle School | All 5 CPS SCA60KTL inverters online and producing as of Jun 9 at 6:00 PM EDT under light rain. Today's peak hourly output was ~215 kW around 2:00 PM, consistent with overcast conditions. 30-day Energy Performance Index averages 0.78 with inverter availability at 100%. Production totals 44.5 MWh vs. 56.9 MWh estimated (78%), reflecting frequent rain in the period rather than a discrete event. Inverters 2 and 3 consistently produce ~30â35% less than Inverter 1 across every daylight hour, flagged by the rule tool as low energy ratios (0.67 and 0.62) with excessive residual loss. This is a persistent performance issue worth field investigation (string-level checks, combiner/fuses). Meter-to-inverter ratio is 0.99 (normal). Sampled Inverter 1 model losses show ~10% soiling loss as the main contributor. Forecast is light rain with highs 82â91Â°F through Jun 12; expect continued subdued production.
S54553 | Butler Maple | All hardware is communicating as of Jun 9 around 5:05 PM PDT, and SMA SC4000 Inverter-1 is producing normally, reaching ~3.4 MW midday under light rain conditions. Site is operating normally with no active production events. 30-day Energy Performance Index averages 1.01 and inverter availability is 100%. 30-day production is 1080 MWh, ~116% of estimate. Sampled-inverter PV model losses show typical DC/AC age (~3%) and soiling (~1%); no major losses identified. Tracker losses are negligible (<4 kWh/day). Meter-to-inverter ratio is 0.99, normal. The rule tool flagged a high energy ratio (~1.21) and SEL-351 Relay default alerts not enabled â review sensor calibration and relay alert configuration. Forecast calls for light rain Jun 10, then clear skies Jun 11â12 with highs of 75â79Â°F, favorable for production.
S54613 | Warbler | All 32 Sungrow SG125 inverters are online and communicating as of Jun 9 at 8:06 PM EDT, with all balance-of-plant devices reporting normally. Today's production was limited by cloud cover; recent clear days (Jun 3â5) reached the 4 MW AC cap during midday hours per the production and expected chart. No discrete production events in the last two weeks. Day-to-day variability on May 22â26 and Jun 1â2 aligns with weather, not equipment issues. 30-day Energy Performance Index averaged 0.88 and inverter availability 97%. Sampled-inverter PV model losses show ~8% residual and ~7% combined age-related losses; no major event-driven losses. Meter-to-inverter ratio 0.99, normal. Rule tool clean; no active alerts. Forecast calls for light rain and highs to 99Â°F Jun 10â12; expect reduced output and possible high-temperature derating.
S54681 | Eagle | All 24 CPS SCH125kTL inverters are online and producing in line with peers as of Jun 9 at 8:06 PM EDT, with current output tapering normally near sunset under light rain. Inv-8 shows a persistent ~25% deficit vs. peers (capped near 75 kW during midday hours) visible across recent days in the production chart, coincident with an active External Fan Err fault triggered Jun 9 at 3:42 PM. Classify as partial capability on ~125 kW (~3% of site); ongoing impact ~150 kWh/day. 30-day EPI averages 0.97 with availability at 99%. No major losses identified on the sampled inverter. Meter-to-inverter ratio is 0.99 â normal. Rule tool reports stale comm/weather flags from earlier in the day; hardware table shows all devices uploading within minutes â disregard as stale. Forecast: rain and light rain through Jun 12, highs 79â82Â°F. Expect reduced but normal production.
S59656 | Whitetail | All 80 SunGrow inverters online and reporting as of Jun 9 at 8:06 PM EDT, with the site producing normally through the day under light rain. Current weather is 77Â°F with light rain; peak hourly output reached ~9.4 MW around midday per the production and expected chart. 30-day EPI averages 0.94 and inverter availability 99%. Production-to-estimate ratio is 91%. Sampled-inverter PV model losses show no major losses; tracker lost energy is 0 kWh over 7 days. Meter-to-inverter ratio is 0.99 (normal). Active alerts: a Tracker Control 2.1 E-Stop/Tracking Disabled fault (Jun 9, 7:04 PM) â no tracker energy loss observed; an Aug 2025 comm-loss alert on the original GameChange Tracker Control remains stale. Rule tool flags ~5â6% soiling on inverters 22, 39, 42, and a POA sensor tilt/azimuth misconfiguration worth review. Forecast: light rain with highs 93â99Â°F through Jun 12; expect moderate weather-driven production variability.
S63837 | Bulloch 1B | All 24 inverters online and reporting as of Jun 9 at 8:07 PM EDT, with the site producing 24,000 kWh today against a 24,475 kWh estimate. Current conditions are clear and 82Â°F at sunset, so production is finished for the day. 30-day Energy Performance Index averages 0.99 with inverter availability at 100% over the last 10 days. PV model losses on the sampled inverter show no major issues; tracker lost energy averages ~76 kWh/day, minor. Meter-to-inverter ratio is 0.98, normal. The rule tool flagged three trackers stuck at fixed angles (Position A1 S 22, S 54, S 79) and an average error of 6.2Â° on S 46 â worth field verification but low energy impact. Forecast is clear to light rain with highs reaching 97Â°F by Jun 12; monitor for possible high-temperature derating midweek.
S63838 | Bulloch 1A | All 28 inverters online and reporting fresh telemetry as of Jun 9 at 8:07 PM EDT, with the site past sunset under clear 82Â°F skies. Earlier today the site reached ~3.0 MW around noon, consistent with AC capacity, though afternoon production was variable with passing clouds. Over the last 30 days, the site averaged an EPI of 0.98 and 99.9% inverter availability. Sampled-inverter PV model losses show only minor age and soiling losses; no major losses identified. Meter-to-inverter ratio is 0.98, normal. The rule tool flags Tracker "Position A1 S 16" stuck at 0Â° and AE Smart UPS default alerts not set â monitoring items only. Tracker losses remain small (~24 kWh on Jun 9). Forecast: clear Jun 10, light rain Jun 11, clear Jun 12 with highs reaching 97Â°F â monitor for heat derating.
S63839 | Richmond | All 24 inverters online and producing as of Jun 9 at 8:07 PM EDT, with clear skies and 82Â°F. Current-day production is tracking expected output closely, with a peak around 2.6 MW midday. 30-day Energy Performance Index averages 0.99 and inverter availability is 100% over the last 9 days (site 30-day 99.7%). Sampled-inverter PV model losses show no notable findings; tracker losses are minor (~30â55 kWh/day). Meter-to-inverter ratio is 0.98, normal. The rule tool flags two NCU 1 trackers stuck (Position A1 S 10 at 22.9Â°, A1 S 56 at -21.3Â°) and inverter-group configuration items; impact is limited based on tracker losses. Forecast: clear Jun 10, light rain Jun 11â12 with highs to 99Â°F â some heat derating possible.
S63840 | Upson | All 24 inverters online and reporting as of Jun 9 at 8:07 PM EDT, with the site in post-sunset hours. Recent days have shown variable production consistent with mixed insolation; Jun 8 and Jun 9 ran well below clear-sky days earlier in the week per the production and expected chart. 30-day Energy Performance Index averages 0.96 with inverter availability at 100%. Sampled-inverter PV model losses show no notable items; tracker losses are under 1 kWh/day. Meter-to-inverter ratio is 0.98 over 30 days â normal. The rule tool flags a POA insolation mismatch (+61% vs other sensors) on the Kipp & Zonen SMP-12 POA pyranometer and low BPOA insolation â review sensor calibration/tilt as this can bias EPI. AE Smart UPS default alerts unset; meter PF near zero noted. Forecast is clear with highs 88â93Â°F through Jun 12 â favorable production conditions.
S64602 | McLean | All 40 inverters communicating as of Jun 9 at 8:07 PM EDT, with the most recent uploads within minutes. Site is producing under light rain after a cloudy afternoon; peak output today reached ~4.7 MW around 11 AM. 30-day Energy Performance Index averages 0.93 with no major drops, and inverter availability is 100% in the past week (site 30-day: 99.83%). No notable PV model losses on the sampled inverter; tracker lost energy runs ~50â125 kWh/day, a minor performance drag tied to several stuck/erroring tracker rows. Meter-to-inverter ratio is 0.98, normal. Monitoring flags: PYRANOMETER - BPOA (PY2) offline since Jun 16, 2025 (equipment repair needed); Solar FlexRack tracker slave SOC alarms (S63, S81) since Apr 30; multiple tracker positions reading 0Â° with ~26Â° average error on S10/S63/S81 per the rule tool. Forecast: light rain with highs climbing to 100Â°F by Jun 12 â expect humid, partly clouded production and monitor for heat derating.
S64603 | Shorthorn | All 72 inverters communicating as of Jun 9 at 8:08 PM EDT, with production tapering normally into evening under light rain. Conditions are intermittently cloudy, consistent with reduced midday output today. No production events in the reporting window. A brief site dip on Jun 5 (EPI 0.81, availability 88%) recovered the same day. 30-day EPI averages 0.97 with inverter availability at 99%. Sampled-inverter losses and tracker losses are minor. Meter-to-inverter ratio is 0.98 (normal). Open tracker alerts on ST1 (e-stop, comm loss since Jun 9 at 10:18 AM) and ST2 (low SoC), plus a rule tool flag noting several trackers with elevated position error or stuck at 0Â°. A production meter current mismatch alert (A/B/C phases) triggered Jun 9 at 7:44 PM â worth monitoring for CT/wiring issues. Forecast is light rain with highs 95â100Â°F through Jun 12; expect variable output and possible heat derating.
S65216 | Green Solar | Inverter 1 is online and producing, last reporting at 5:05 PM PDT on Jun 9, with all other hardware communicating normally. Current output is tracking expected energy closely under clear skies and 57Â°F. No production events occurred in the reporting period. Variable output on Jun 3, Jun 5, and Jun 8 reflects intermittent cloud cover, not equipment issues. 30-day Energy Performance Index averaged 0.99 with inverter availability at 99%. Production reached 99% of estimate. No major losses identified in the sampled inverter PV model losses or tracker losses. Meter-to-inverter ratio is 0.99, normal. The rule tool high energy ratio flags reflect partial-day data and are not actionable. Forecast is clear with highs rising to 82Â°F by Jun 12 â favorable production conditions with no derating concerns.
S65784 | Washington Solar | All 40 inverters communicating as of Jun 9 at 8:08 PM EDT, with site availability at 100% over the last 30 days. Current conditions are light rain at 77Â°F, and today's production reflects a cloudy/rainy profile, peaking near 3.7 MW at 1:00 PM versus ~5 MW expected. The INVERTER 6 invalid-data warning that triggered at 8:03 PM is a brief end-of-day comm blip; Last Update is current. The 30-day Energy Performance Index averages ~1.16, consistently above 1.1, suggesting a PV model or POA sensor calibration issue worth review. 30-day production is 1,246 MWh (94% of estimate). Meter-to-inverter ratio is 0.98 (normal). Rule tool flags stuck VacA/VacB/VacC telemetry across all 40 inverters and many trackers stuck at 0Â° â data-quality flags, not production impacts (tracker losses <3 kWh/day). Forecast: light rain through Jun 10, then hot (97Â°F) Jun 11â12 â monitor for thermal derate.
S65785 | Harding Solar | All 24 inverters online and producing normally as of Jun 9 at 8:08 PM EDT, with the site tracking expected output closely through the afternoon on the production and expected chart. Clear skies, 77Â°F, light winds. 30-day Energy Performance Index averages 0.96 with inverter availability at 100%. Production totaled 812 MWh vs. 791 MWh estimate (103%). Sampled-inverter PV model losses and tracker losses (~7 kWh/day) are minor. Meter-to-inverter ratio is 0.98, normal. The rule tool flags excessive soiling on Inverters 3, 8, and 17 (~9-11%) and a tracker position error of ~33Â° on TCU 87. An ALSOENERGY Smart UPS Battery Over Temperature alert triggered Jun 9 at 9:14 AM; the UPS continues reporting. Forecast: light rain and highs 90-97Â°F Jun 10-12, which may modestly reduce output.
S65786 | Whitehall Solar | All 16 inverters online and producing as of Jun 9 at 8:08 PM EDT, with the site reaching ~2,000 kW peak hourly output earlier today per the production and expected chart. Light rain and variable cloud cover suppressed midday output today and on Jun 7â8, consistent with weather. 30-day Energy Performance Index averaged 0.92 and inverter availability averaged 100%. Sampled-inverter PV model losses show no major issues; tracker losses are negligible (~2â5 kWh/day). Meter-to-inverter ratio is 0.98, normal. Rule tool flags TCU 24 stuck at 0Â° and a weather station module-temp sensor reading below ambient â review the back-of-module sensor calibration, as it can affect expected energy. Forecast calls for light rain and highs near 93â100Â°F through Jun 12; high temperatures may cause minor inverter derating but no stow risk with light winds.
S65787 | Sunflower Solar | All 80 inverters are communicating and operating as of Jun 9 at 8:09 PM EDT, with the production meter, weather station, and trackers reporting normally. Light rain is on site at 79Â°F, with reduced afternoon production today consistent with overcast conditions. No production events in the last two weeks. Daily output has tracked the site performance estimate closely, with full-capacity hours (~9,996 kW) observed Jun 3â5. 30-day EPI averages 0.97 and inverter availability is 99%. No major losses identified on the sampled inverter; tracker losses are minor (~24â50 kWh/day). Meter-to-inverter ratio is 0.98 (normal). A May 17 transformer 90Â°C liquid-temp fault and several rule tool tracker-error and POA insolation-mismatch flags are open with no production correlation; worth review for sensor and tracker alignment. Forecast is light rain with highs 93â99Â°F through Jun 12; expect variable production and some heat-related derate risk.
S65788 | Gray Fox Solar | All 40 inverters communicating as of Jun 9 at 8:09 PM EDT, with site producing through a light-rain afternoon. Today's peak hourly output reached ~4.9 MW around noon before clouds and rain reduced afternoon output, yielding a partial-day EPI of 0.68. Recent days track expected output closely. No production events in the last two weeks. Jun 8 and Jun 9 both saw weather-driven dips consistent with rain, not equipment issues. 30-day EPI averages 0.88 and inverter availability 97%. Production reached 91% of monthly estimate. Sampled-inverter and tracker losses show nothing notable. Meter-to-inverter ratio is 0.98, normal. One Rule Tool informational alert from Jun 1 has no production correlation. Forecast is light rain to rain Jun 10â12 with highs reaching 100Â°F by Jun 12; expect weather-limited output and possible temperature derating mid-week.
S65918 | C & B Graham Energy | Site producing through evening with light rain; meter shows 22,830 kWh today across METER 2 and METER 3. Several inverters are confirmed offline based on hourly production: INV-4 (since Jun 9 ~1 PM EDT, forced outage â Shutdown Command), INV-7 and INV-9 (since Jun 2, forced outages), INV-13 (since May 21), INV-17 (since Apr 22), INV-22 (Jun 9 ~5 PM, arc fault), INV-23 (since Apr 10), INV-35 (since Apr 6). INV-14 tripped Jun 9 7:21 AM (hardware self-test) but resumed. Combined ~1.4 MW offline; today's loss ~6â8 MWh vs. ~61 MWh daily estimate. 30-day production totals 740 MWh vs. ~1,782 MWh estimate (42%), reflecting cumulative inverter outages and rainy periods; EPI and availability are uncomputable due to weather station data issues. METER 1 not reporting since Apr 27; meter-to-inverter ratio on reporting meters ~0.79 â low, likely metering data gap. Multiple active fault and comm alerts outstanding, plus pyranometer/weather station offline. Forecast: rain and heavy rain Jun 10â12, reduced production expected.
S66000 | Auburn Solar | All hardware is communicating as of Jun 9 at 5:09 PM PDT, with Inverter 1 producing normally through the afternoon under light rain conditions. Today's production tracks expected output closely, peaking near 2.0 MW. Over the last 30 days, the site is performing well: EPI averages 1.09 and inverter availability is 100%. Total production of 553 MWh is 123% of estimate. The persistently elevated EPI (>1.1 on several days) suggests a possible PV model or pyranometer calibration drift worth reviewing. Tracker losses are negligible (<13 kWh/day). Meter-to-inverter ratio is 1.01, slightly elevated but consistent over the period â worth monitoring CT/meter configuration. No active alerts and rule tool is clean. Forecast: light rain Jun 10, then clear and warm (75â77Â°F) Jun 11â12, supporting strong production.
S66001 | Sheridan Solar | Inverter 1 is online and producing, with hardware last update at Jun 9 at 5:09 PM PDT. Current conditions are light rain at 59Â°F, and today's production reached ~2.5 MW at midday under variable irradiance. 30-day Energy Performance Index averages 1.02 and inverter availability is 100%. Total production of 829 MWh is 114% of estimate. No major losses identified on the sampled inverter; tracker losses are minimal (<25 kWh/day). Meter-to-inverter ratio is 0.99 (normal). The rule tool flagged a high energy ratio (1.12) and elevated weather station temperature â worth monitoring for sensor calibration but no production impact. Forecast: light rain Jun 10, clearing Jun 11â12 with highs to 79Â°F. Favorable production conditions ahead.
S66930 | Elk Solar | Inverter 01.02 has been offline since May 27 at 3:29 AM EDT (forced outage, ~750 kWh/day downtime loss on sampled inverter). Inverter 01.15 also shows zero production with stuck AC telemetry â concurrent outage. Inverters 01.08â01.14 show reduced availability ~30% with ~575â633 kWh/day downtime loss each. Combined ~9 inverter outage represents ~1.1 MW affected capacity, ~5.6 MWh/day loss, ~78 MWh over 14 days. Today's site peak was ~4.3 MW around noon under light rain; weather-limited. 30-day inverter availability 95%; actual/expected 90%. Inverters 01.01 and 01.05 show low energy ratios (0.34, 0.50) â investigate. Production meter reports zero (meter/inverter ratio undefined); voltage calc 173% of meter power â CT/metering issue. NCU 1 and NCU 2 show stuck trackers and abnormal motor currents; tracker losses ~44â73 kWh/day. Forecast: rain through Jun 12, highs 93â100Â°F â expect weather-limited output and possible thermal derating.
S68112 | Wallace Solar | Inverter 1 is online and producing, with the hardware last reporting at 5:07 PM PDT on Jun 9. Light rain is reducing output today, with a peak hourly output of ~2.4 MWh this morning per the production chart. No production events in the last 30 days. Inverter availability held at 100%. The 30-day EPI averaged 1.07, persistently above 1.0, suggesting a PV model or POA calibration issue rather than a plant problem. Tracker losses were minimal (~0.9â59 kWh/day). Meter-to-inverter ratio is 0.99, normal. The rule tool flags POA insolation +55% higher than other sensors and low BPOA â consistent with the elevated EPI and warrants a pyranometer azimuth/tilt and calibration check. Forecast: light rain Jun 10, then clear and warm Jun 11â12 (75â79Â°F), favorable for production.
S68113 | Marble Solar | Marble Solar is operating normally as of Jun 9 at 5:09 PM PDT. All hardware is communicating, and Inverter 1 produced about 2.6 MW peak earlier today under clear skies and 61Â°F temperatures. 30-day Energy Performance Index averages 0.99 with inverter availability at 100%. Total production of 758 MWh is 107% of estimate. No major losses identified in the PV model for the sampled inverter; tracker losses are minimal (under 26 kWh/day). Meter-to-inverter ratio is 0.99, within normal range. No active alerts or monitoring flags. Forecast shows light rain Jun 10, then clear and warm (75â77Â°F) Jun 11â12 â favorable production conditions ahead.
S70532 | Longleaf Pine Solar, LLC | All 40 inverters are online and producing as of Jun 9 at 8:10 PM EDT, with site output tracking irradiance on a light-rain day per the production and expected chart. A site-wide outage occurred Jun 3â4, with zero meter and inverter production both days visible on the production meter chart. Cause is undetermined from available data. Estimated loss ~83 MWh (2 days, 100% capacity, ~42 MWh/day expected). Production fully recovered Jun 5. A similar full-site outage occurred May 17â19, contributing to the EPI dips on those dates. 30-day EPI averages 1.00 excluding outage days; inverter availability is 93%, dragged by the Jun 3â4 event. Meter-to-inverter ratio is 0.98 (normal). Tracker Controller 1 has been offline since Jun 3 with minimal energy impact (~16â30 kWh/day site-wide); TCU 33 shows a 64Â° tracker error per active alerts. Two transformer vacuum-fault alerts remain unacknowledged. Forecast: light rain and highs to 99Â°F through Jun 12; no production risk expected.
S70645 | Williams Solar, LLC | INVERTER A20 has been offline since Jun 5 with zero production while peers operate normally. The meter-to-inverter ratio of 0.97 confirms a true outage, not a comm loss. A grid overvoltage fault on Jun 8 at 3:10 PM EDT followed by a device communication alert at 3:39 PM points to a forced outage. The other 39 inverters are online and producing normally under clear skies. INVERTER A20 forced outage (Jun 5âpresent, ongoing ~5 days, 125 kW / 2.5% of site capacity). Estimated loss ~5 MWh (5 days Ã ~1 MWh/day expected per PV Model Losses for the sampled inverter). 30-day EPI averages 0.98; inverter availability 99%. Tracker losses minimal (~23 kWh/day). Forecast brings rain and highs near 100Â°F Jun 10â12; possible heat derating and reduced irradiance.
S55935 | Manuel Lawrence Dairy | Site status cannot be fully assessed â hardware list, production charts, availability, and EPI data are all unavailable for this reporting period. No active alerts are present. Current site time is Jun 9 at 5:11 PM PDT, with clear skies and 91Â°F. Conditions are favorable for production, but actual output cannot be confirmed from available data. The rule tool reports 0% inverter availability and is unable to calculate PV losses across all 15 CPS SCA 60KTL-DO inverters or energy ratio at the Elkor production meter. The IMT reference cell is also reporting invalid module temperature and irradiance, and default alerts are not set on the SFR TDP 2.0 solar tracker. These findings cannot be validated against meter-to-inverter ratio or production charts due to the data retrieval failures noted above. Forecast is clear and hot through Jun 12, with highs reaching 109Â°F. Inverter derating is possible during peak afternoon hours later this week. Data retrieval should be restored to enable proper performance assessment.

## Status Cross-Tab
comm_status | prod_status | count
All Communicating | Unknown | 4
Partial / Issues | Below Expected | 1
Partial / Issues | Unknown | 8
Unknown | Below Expected | 4
Unknown | On Track | 1
Unknown | Unknown | 17