SolRiver Solar Portfolio

Weekly Health Report

Report Period: June 1–8, 2026

# Executive Summary

During the week of June 1–8, your portfolio experienced 32 total alerts affecting 15 sites. Of these, 20 alerts remain unresolved and require immediate attention. The primary concern is C & B Graham Energy, which accounted for 41% of weekly alerts (13 of 32).

# Critical Issues Requiring Immediate Action

## 1. C & B Graham Energy — 9 Unresolved Alerts

- Inverter Faults (Solectria XGI 1000/1500 Series) — Multiple units reporting low voltage conditions, phase lock loop failures, and AC switch shutdowns. Impact: Likely power loss from affected units.

- Device Communication Failures (3 instances) — Wiring problems suspected between devices and gateway. Impact: Loss of monitoring and control.

- Solar FlexRack Tracker Alert — System monitor detected out-of-range/fault condition. Impact: Tracker may not be optimizing for sun position.

## 2. Eagle — 4 Unresolved Alerts

- Inverter Insulation Resistance Low — Isolation error detected. Risk of safety/efficiency issue.

- External Fan Errors — Multiple cooling fan failures. Risk of thermal shutdown.

- Device & Gateway Heartbeat Failures — Wiring or power supply issue between gateway and devices.

## 3. Longleaf Pine Solar, LLC — 2 Unresolved Alerts

- Transformer Vacuum Fault — Pressure reading is critically low (< –5 psi). Oil cooling may be compromised.

- Device Communication Loss — Wiring/connection issue.

# Most Problematic Sites

| Site Name | Total Alerts | Unresolved |
| --- | --- | --- |
| C & B Graham Energy | 13 | 9 |
| Eagle | 4 | 4 |
| Longleaf Pine Solar, LLC | 2 | 2 |

# Alert Summary by Type

- Rule Tool Alerts: 11 — Communication and performance test failures across multiple sites.

- Device Communication: 5 — Wiring/connection issues between gateways and field devices.

- Inverter Faults (Solectria XGI): 7 — Low voltage, phase lock loop, and shutdown alerts.

- String Inverter Faults (.Chint/Solectria/Canadian): 3 — Insulation and fan errors.

- Other: 6 (Tracker, Transformer, Heartbeat alerts)

# Immediate Action Plan

- C & B Graham Energy (Priority 1) — Schedule site visit within 48 hours. Inspect inverter electrical connections, validate low-voltage readings, and check AC switch status. Device communication failures suggest a wiring/connector issue.

- Eagle (Priority 1) — Address external fan failures and heartbeat/gateway communication issues. Likely wiring or power supply at the gateway.

- Longleaf Pine Solar, LLC (Priority 1) — Transformer vacuum fault is critical. Contact transformer OEM immediately to assess cooling system status.

- Follow-up — After resolving critical issues, review remaining 8 unresolved alerts and acknowledge/reassign as needed.

Generated: June 9, 2026