## Resolved Alerts
Contractor | Project | Equip | SubPart | Issue4Work | Work | CreateLoss | Comments | Repair (P) | Unit ID | QTY | Bucket | Start Date | Start Time | End Date | End Time | alert_id | event_type_code | event_type_name
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/6/2026 | 10:24 am | 6/6/2026 | 11:16 am | 153791455 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/6/2026 | 10:32 am | 6/6/2026 | 10:41 am | 153792895 | 551 | Power Meter Check 2.0
NRCO | Warbler | DAS |  |  |  | 0 | Battery Mode Activated |  |  | 1 | Repair | 6/6/2026 | 11:18 am | 6/6/2026 | 11:38 am | 153796056 | 548 | Phoenix Contact - Quint UPS Alerts
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/6/2026 | 7:01 pm | 6/6/2026 | 7:24 pm | 153790261 | 551 | Power Meter Check 2.0
TMI | Eagle | Inverter | DC Wire | Repair | DC Wire - Repair | 1 | Insulation Resistance Low - IsolationErr |  | 2 | 1 | Repair | 6/6/2026 | 7:02 pm | 6/9/2026 | 6:22 pm | 153841427 | 438 | .Chint / Solectria / Canadian String Inv Faults
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/7/2026 | 12:08 am | 6/7/2026 | 12:58 am | 153792341 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/7/2026 | 10:40 am | 6/7/2026 | 11:36 am | 153873987 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/7/2026 | 10:44 am | 6/7/2026 | 10:48 am | 153898254 | 551 | Power Meter Check 2.0
NRCO | Williams | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | A20 | 1 | Outage | 6/7/2026 | 11:25 am | 6/7/2026 | 2:31 pm | 153901865 | 630 | Sungrow Inverter Fault Alert
NRCO | Williams | Inverter |  | Offline | Offline | 1 | Grid undervoltage |  | A20 | 1 | Repair | 6/7/2026 | 6:08 pm | 6/7/2026 | 6:09 pm | 153943150 | 630 | Sungrow Inverter Fault Alert
NRCO | Williams | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/7/2026 | 7:16 pm | 6/7/2026 | 7:22 pm | 153949591 | 3618 | Phoenix Contact - Quint UPS Alerts (QUINT4 EIP)
Solential | Graham | Inverter |  | Repair | Repair | 1 | Over voltage current Internal hardware failure |  | 4 | 1 | Repair | 6/7/2026 | 8:00 pm | 6/7/2026 | 8:08 pm | 153954077 | 2899 | Solectria XGI 1500 Series - Fault Alert
NRCO | Williams | Inverter |  | Grid Voltage Imbalance | Grid Voltage Imbalance | 1 | Grid voltage unbalance |  | A20 | 1 | Repair | 6/7/2026 | 8:21 pm | 6/7/2026 | 8:23 pm | 153956115 | 630 | Sungrow Inverter Fault Alert
NRCO | Williams | Inverter |  | Grid Phase Voltage High | Grid Phase Voltage High | 1 | Grid overvoltage |  | A20 | 1 | Repair | 6/7/2026 | 9:13 pm | 6/7/2026 | 9:15 pm | 153961048 | 630 | Sungrow Inverter Fault Alert
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/7/2026 | 10:34 pm | 6/8/2026 | 12:37 am | 153892894 | 551 | Power Meter Check 2.0
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/7/2026 | 11:04 pm | 6/7/2026 | 11:54 pm | 153768484 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/8/2026 | 12:15 am | 6/8/2026 | 12:51 am | 153974174 | 551 | Power Meter Check 2.0
NRCO | Williams | DAS |  |  |  | 0 | Battery Voltage Low |  |  | 1 | Repair | 6/8/2026 | 6:06 am | 6/8/2026 | 6:10 am | 153991490 | 3618 | Phoenix Contact - Quint UPS Alerts (QUINT4 EIP)
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/8/2026 | 10:29 am | 6/8/2026 | 10:38 am | 154001117 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Weather station |  | Weather station | 0 | Mid day module temperature low module 1: 28.6 °C |  | 1 | 1 | Repair | 6/8/2026 | 3:55 pm | 6/8/2026 | 4:59 pm | 152939504 | 499 | Weather Station Alert
NRCO | Shorthorn | Inverter | Fan | Repair | Fan - Repair | 1 | Fan failure |  | 4 | 1 | Repair | 6/8/2026 | 4:08 pm | 6/8/2026 | 4:48 pm | 154034183 | 630 | Sungrow Inverter Fault Alert
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/8/2026 | 10:24 pm | 6/9/2026 | 12:41 am | 153978276 | 551 | Power Meter Check 2.0
TMI | GSR-Green | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/8/2026 | 10:25 pm | 6/8/2026 | 10:48 pm | 153865924 | 551 | Power Meter Check 2.0
NRCO | Washington | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/8/2026 | 10:46 pm | 6/8/2026 | 11:39 pm | 152770246 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/8/2026 | 11:11 pm | 6/9/2026 | 12:18 am | 153999940 | 551 | Power Meter Check 2.0
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/8/2026 | 11:24 pm | 6/8/2026 | 11:56 pm | 153997727 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/9/2026 | 12:18 am | 6/9/2026 | 12:51 am | 153999026 | 551 | Power Meter Check 2.0
TMI | GSR-Green | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Power phase error/Alerts are too sensitive and happening during the night. Low irradiance in the area is also effecting these alerts. |  |  | 1 | Repair | 6/9/2026 | 1:12 am | 6/9/2026 | 2:09 am | 154085477 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/9/2026 | 10:41 am | 6/9/2026 | 12:51 pm | 154109089 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/9/2026 | 10:44 am | 6/9/2026 | 10:52 am | 154111515 | 551 | Power Meter Check 2.0
Solential | Graham | Inverter |  | Fault | Fault | 1 | Hardware self test failure |  | 14 | 1 | Repair | 6/9/2026 | 11:21 am | 6/10/2026 | 10:15 am | 154115173 | 2899 | Solectria XGI 1500 Series - Fault Alert
Solential | Graham | Inverter |  | Arc Fault | Arc Fault | 1 | Arc fault detected |  | 22 | 1 | Repair | 6/9/2026 | 9:30 pm | 6/10/2026 | 10:17 am | 154194239 | 2899 | Solectria XGI 1500 Series - Fault Alert
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/9/2026 | 10:01 pm | 6/9/2026 | 11:55 pm | 154081703 | 551 | Power Meter Check 2.0
NRCO | Washington | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/9/2026 | 11:12 pm | 6/9/2026 | 11:48 pm | 154118804 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/9/2026 | 11:44 pm | 6/10/2026 | 12:18 am | 154205405 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/10/2026 | 10:57 am | 6/10/2026 | 10:58 am | 154254803 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/10/2026 | 11:13 am | 6/10/2026 | 11:47 am | 154253124 | 551 | Power Meter Check 2.0
Solential | Graham | Inverter |  | Fault | Fault | 1 | Inverter Faults Detected ¦ Open phase detected |  | 20, 25 | 2 | Repair | 6/10/2026 | 12:51 pm | 6/10/2026 | 1:07 pm | 154267962 | 1037 | Solectria XGI 1000 Series - Fault Alert
Solential | Graham | Inverter | Fan | Repair | Fan - Repair | 1 | External Fan Damaged |  | 1 | 1 | Repair | 6/10/2026 | 1:05 pm | 6/10/2026 | 11:51 pm | 154269682 | 2899 | Solectria XGI 1500 Series - Fault Alert
Solential | Graham | Inverter |  | Repair | Repair | 1 | High voltage 1 (HV1) |  | 20 | 1 | Repair | 6/10/2026 | 2:07 pm | 6/10/2026 | 2:11 pm | 154277485 | 2899 | Solectria XGI 1500 Series - Fault Alert
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/10/2026 | 6:26 pm | 6/10/2026 | 7:02 pm | 154247142 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/10/2026 | 10:29 pm | 6/10/2026 | 11:33 pm | 154213279 | 551 | Power Meter Check 2.0
Solential | Graham | Inverter |  | Repair | Repair | 1 | Internal hardware failure |  | 14 | 1 | Repair | 6/10/2026 | 10:47 pm | 6/10/2026 | 10:48 pm | 154352834 | 2899 | Solectria XGI 1500 Series - Fault Alert
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/11/2026 | 12:25 am | 6/11/2026 | 12:58 am | 154256149 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/11/2026 | 10:38 am | 6/11/2026 | 10:42 am | 154402827 | 551 | Power Meter Check 2.0
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/11/2026 | 11:30 am | 6/11/2026 | 11:58 am | 154362734 | 551 | Power Meter Check 2.0
Solential | Graham | Inverter |  | Repair | Repair | 1 | High voltage 1 (HV1) Low voltage 1 (LV1) |  | 16 | 1 | Repair | 6/11/2026 | 3:31 pm | 6/11/2026 | 3:39 pm | 154438921 | 2899 | Solectria XGI 1500 Series - Fault Alert
Solential | Graham | Tracker | TCU | Communication | TCU - Communication | 1 | Slave Alarms S 10: SW version is a test build for accelerated time test Slave Alarms S 16: SW version is a test build for accelerated time test |  | 10, 16 | 2 | Repair | 6/11/2026 | 3:39 pm | 6/18/2026 | 3:45 pm | 154439205 | 593 | Solar FlexRack Tracker Alert
Solential | Graham | Inverter |  | Offline | Offline | 1 | Shutdown Command - AC Switch |  | 3 | 1 | Repair | 6/11/2026 | 4:15 pm | 6/11/2026 | 4:27 pm | 154443727 | 2899 | Solectria XGI 1500 Series - Fault Alert
NRCO | Shorthorn | Tracker | TCU | Battery Low | TCU - Battery Low | 1 | Slave Alarms S 94: System Monitor has detected an out of range or fault condition (check system monitor status) Slave Alarms S 25: State Of Charge is under the critical threshold |  | 25, 94 | 2 | Repair | 6/11/2026 | 4:39 pm | 6/12/2026 | 6:03 am | 154446801 | 974 | Solar FlexRack Tracker Alert (revG)
TMI | GSR-Rio | DAS | Weather station |  | Weather station | 0 | Mid day module temperature low module 1: 35.7 °C |  | 1 | 1 | Repair | 6/11/2026 | 5:58 pm | 6/12/2026 | 3:38 pm | 154039291 | 499 | Weather Station Alert
NRCO | Bulloch1 | Tracker | TCU | Communication | TCU - Communication | 1 | Slave Alarms S 41: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 41 | 1 | Repair | 6/11/2026 | 6:51 pm | 6/11/2026 | 9:42 pm | 154157971 | 974 | Solar FlexRack Tracker Alert (revG)
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/11/2026 | 7:43 pm | 6/11/2026 | 8:10 pm | 154396466 | 551 | Power Meter Check 2.0
NRCO | Washington | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/11/2026 | 11:26 pm | 6/12/2026 | 12:02 am | 154259816 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/11/2026 | 11:30 pm | 6/12/2026 | 12:15 am | 154404705 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/12/2026 | 12:18 am | 6/12/2026 | 12:39 am | 154496068 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/12/2026 | 12:25 am | 6/12/2026 | 12:58 am | 154499294 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/12/2026 | 10:36 am | 6/12/2026 | 10:44 am | 154525741 | 551 | Power Meter Check 2.0
NRCO | Longleaf | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/12/2026 | 1:28 pm | 6/12/2026 | 11:47 pm | 154542755 | 3618 | Phoenix Contact - Quint UPS Alerts (QUINT4 EIP)
NRCO | Whitetail | Tracker | TCU | Communication | TCU - Communication | 1 | Individual Tracker Alarm91: No Communication Individual Tracker Alarm92: No Communication ¦ Individual Tracker Alarm1: No Communication Individual Tracker Alarm2: No Communication ¦ Individual Tracker Alarm181: No Communication Individual Tracker Alarm182: No Communication |  | 1-2, 91-92, 181-182 | 6 | Repair | 6/12/2026 | 1:42 pm | 6/12/2026 | 2:30 pm | 154544040 | 863 | Gamechange Tracker Alert
NRCO | Shorthorn | Tracker | TCU | Communication | TCU - Communication | 1 | Slave Alarms S TCU 1: System Monitor has detected an out of range or fault condition (check system monitor status) ¦ Slave Alarms S 13: System Monitor has detected an out of range or fault condition (check system monitor status) Slave Alarms S 21: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 13, 21, ST0 | 3 | Repair | 6/12/2026 | 4:52 pm | 6/12/2026 | 7:29 pm | 154565712 | 974 | Solar FlexRack Tracker Alert (revG)
NRCO | Gray Fox | Tracker | Motor | Stuck | Motor - Stuck | 1 | TCU Fault45: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 45 | 1 | Repair | 6/12/2026 | 5:37 pm | 6/12/2026 | 5:49 pm | 154571111 | 3635 | Solar FlexRack/OMCO Tracker Alert (revM)
NRCO | Gray Fox | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/12/2026 | 5:53 pm | 6/12/2026 | 6:06 pm | 154572997 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Williams | Tracker | Motor | Stuck | Motor - Stuck | 1 | TCU Fault58: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 58 | 1 | Repair | 6/12/2026 | 7:07 pm | 6/12/2026 | 7:19 pm | 154581722 | 3635 | Solar FlexRack/OMCO Tracker Alert (revM)
NRCO | Bulloch1 | Tracker | TCU | Communication | TCU - Communication | 1 | Slave Alarms S 39: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 39 | 1 | Repair | 6/12/2026 | 7:24 pm | 6/12/2026 | 9:29 pm | 154486502 | 974 | Solar FlexRack Tracker Alert (revG)
NRCO | Longleaf | Xfmr |  | Repair | Repair | 1 | 90 degree liquid temp fault - Temperature greater than 90 C. |  |  | 1 | Repair | 6/12/2026 | 7:53 pm | 6/12/2026 | 11:15 pm | 154587022 | 534 | Transformer Monitor
NRCO | Sunflower | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/12/2026 | 7:59 pm | 6/12/2026 | 8:13 pm | 154587920 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Gray Fox | Tracker | Motor | Stuck | Motor - Stuck | 1 | TCU Fault152: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 152 | 1 | Repair | 6/12/2026 | 8:23 pm | 6/12/2026 | 8:46 pm | 154590338 | 3635 | Solar FlexRack/OMCO Tracker Alert (revM)
NRCO | Gray Fox | Tracker | Motor | Stuck | Motor - Stuck | 1 | TCU Fault16: System Monitor has detected an out of range or fault condition (check system monitor status) TCU Fault90: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 16, 90 | 2 | Repair | 6/12/2026 | 8:25 pm | 6/12/2026 | 8:49 pm | 154590799 | 3635 | Solar FlexRack/OMCO Tracker Alert (revM)
NRCO | Mclean | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/12/2026 | 8:55 pm | 6/12/2026 | 9:40 pm | 154594658 | 548 | Phoenix Contact - Quint UPS Alerts
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/12/2026 | 9:42 pm | 6/12/2026 | 11:51 pm | 154498551 | 551 | Power Meter Check 2.0
NRCO | Longleaf | Site | Recloser | Reclosed | Recloser - Reclosed | 1 | SEL Relay is open |  |  | 1 | Outage | 6/12/2026 | 10:16 pm | 6/14/2026 | 2:30 pm | 154602628 | 604 | SEL Recloser Open Alarm
NRCO | Longleaf | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | A16 | 1 | Outage | 6/12/2026 | 10:20 pm | 6/14/2026 | 2:28 pm | 154603194 | 630 | Sungrow Inverter Fault Alert
NRCO | Washington | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/12/2026 | 10:40 pm | 6/12/2026 | 11:40 pm | 154590274 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/12/2026 | 11:30 pm | 6/13/2026 | 12:18 am | 154526055 | 551 | Power Meter Check 2.0
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/13/2026 | 12:01 am | 6/13/2026 | 12:37 am | 154611098 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch ¦ Power phase error/Alerts are too sensitive and happening during the night. Low irradiance in the area is also effecting these alerts. |  |  | 2 | Repair | 6/13/2026 | 12:11 am | 6/13/2026 | 5:10 am | 154525316 | 551 | Power Meter Check 2.0
NRCO | Whitehall | DAS |  |  |  | 0 | Battery Voltage Low |  |  | 1 | Repair | 6/13/2026 | 1:31 am | 6/13/2026 | 1:33 am | 154617623 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Longleaf | Xfmr |  | Vacuum Vault Pressure Repair | Vacuum Vault Pressure Repair | 1 | Vacuum fault - Pressure less than -5 psi |  |  | 1 | Repair | 6/13/2026 | 8:01 am | 6/14/2026 | 5:21 pm | 154631254 | 534 | Transformer Monitor
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/13/2026 | 10:33 am | 6/13/2026 | 11:42 am | 154636574 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/13/2026 | 10:34 am | 6/13/2026 | 10:44 am | 154638802 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | Tracker | TCU | Battery Low | TCU - Battery Low | 1 | Slave Alarms S 94: System Monitor has detected an out of range or fault condition (check system monitor status) Slave Alarms S 94: State Of Charge is not enough to reach target position in a safe way (safe = ensure the return to stow position and remain with a minimum state of charge). |  | 94 | 1 | Repair | 6/13/2026 | 4:21 pm | 6/13/2026 | 7:25 pm | 154671189 | 974 | Solar FlexRack Tracker Alert (revG)
NRCO | Whitehall | Xfmr |  | Repair | Repair | 1 | 90 degree liquid temp fault - Temperature greater than 90 C. |  |  | 1 | Repair | 6/13/2026 | 4:49 pm | 6/14/2026 | 12:47 am | 154673357 | 534 | Transformer Monitor
NRCO | Gray Fox | Tracker | Motor | Stuck | Motor - Stuck | 1 | TCU Fault53: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 53 | 1 | Repair | 6/13/2026 | 4:57 pm | 6/13/2026 | 5:19 pm | 154674789 | 3635 | Solar FlexRack/OMCO Tracker Alert (revM)
NRCO | Whitetail | Inverter | Fan | Repair | Fan - Repair | 1 | Fan failure |  | 22 | 1 | Repair | 6/13/2026 | 5:41 pm | 6/13/2026 | 6:11 pm | 154679707 | 630 | Sungrow Inverter Fault Alert
NRCO | Richmond | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Voltage missing: Phase A: 0.00 volts |  |  | 1 | Repair | 6/13/2026 | 6:37 pm | 6/13/2026 | 6:40 pm | 154685640 | 551 | Power Meter Check 2.0
NRCO | Whitetail | Tracker | TCU | Stuck | TCU - Stuck | 1 | Individual Tracker Alarm60: Tracking Disabled Individual Tracker Alarm60: E-Stop is pressed |  | 60 | 1 | Repair | 6/13/2026 | 6:38 pm | 6/13/2026 | 6:44 pm | 154686093 | 863 | Gamechange Tracker Alert
NRCO | Richmond | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 4 | 1 | Outage | 6/13/2026 | 6:40 pm | 6/13/2026 | 9:22 pm | 154685767 | 630 | Sungrow Inverter Fault Alert
NRCO | Whitetail | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/13/2026 | 6:43 pm | 6/13/2026 | 7:23 pm | 154686303 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Gray Fox | Tracker | Motor | Stuck | Motor - Stuck | 1 | TCU Fault121: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 121 | 1 | Repair | 6/13/2026 | 6:51 pm | 6/13/2026 | 7:13 pm | 154687159 | 3635 | Solar FlexRack/OMCO Tracker Alert (revM)
NRCO | Gray Fox | Tracker | Motor | Stuck | Motor - Stuck | 1 | TCU Fault55: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 55 | 1 | Repair | 6/13/2026 | 6:53 pm | 6/13/2026 | 7:11 pm | 154687402 | 3635 | Solar FlexRack/OMCO Tracker Alert (revM)
NRCO | Bulloch1 | Tracker | TCU | Communication | TCU - Communication | 1 | Slave Alarms S 11: System Monitor has detected an out of range or fault condition (check system monitor status) Slave Alarms S 39: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 11, 39 | 2 | Repair | 6/13/2026 | 7:08 pm | 6/13/2026 | 9:11 pm | 154689064 | 974 | Solar FlexRack Tracker Alert (revG)
NRCO | Shorthorn | Tracker | TCU | Battery Low | TCU - Battery Low | 1 | Slave Alarms S 94: State Of Charge is not enough to reach target position in a safe way (safe = ensure the return to stow position and remain with a minimum state of charge). Slave Alarms S 25: State Of Charge is under the critical threshold |  | 25, 94 | 2 | Repair | 6/13/2026 | 7:27 pm | 6/14/2026 | 12:07 am | 154690706 | 974 | Solar FlexRack Tracker Alert (revG)
NRCO | Gray Fox | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 1.13 | 1 | Outage | 6/13/2026 | 8:09 pm | 6/13/2026 | 8:21 pm | 154695211 | 630 | Sungrow Inverter Fault Alert
NRCO | Bulloch2 | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/13/2026 | 9:39 pm | 6/13/2026 | 10:19 pm | 154704102 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Gray Fox | Site | Recloser | Reclosed | Recloser - Reclosed | 1 | SEL Relay is open |  |  | 1 | Outage | 6/13/2026 | 9:47 pm | 6/13/2026 | 9:51 pm | 154704867 | 604 | SEL Recloser Open Alarm
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/13/2026 | 10:28 pm | 6/14/2026 | 1:03 am | 154634513 | 551 | Power Meter Check 2.0
NRCO | Washington | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/13/2026 | 11:30 pm | 6/14/2026 | 12:06 am | 154697599 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/14/2026 | 12:02 am | 6/14/2026 | 12:04 am | 154715507 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | Tracker | TCU | Battery Low | TCU - Battery Low | 1 | Slave Alarms S 94: State Of Charge is not enough to reach target position in a safe way (safe = ensure the return to stow position and remain with a minimum state of charge). Slave Alarms S 94: State Of Charge is under the critical threshold |  | 94 | 1 | Repair | 6/14/2026 | 12:19 am | 6/14/2026 | 2:23 am | 154716766 | 974 | Solar FlexRack Tracker Alert (revG)
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/14/2026 | 12:28 am | 6/14/2026 | 1:01 am | 154717022 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Weather station |  | Weather station | 0 | Mid day module temperature low module 1: 17.5 °C |  | 1 | 1 | Repair | 6/14/2026 | 5:52 pm | 6/15/2026 | 2:26 pm | 154559274 | 499 | Weather Station Alert
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/14/2026 | 7:35 pm | 6/14/2026 | 8:07 pm | 154741327 | 551 | Power Meter Check 2.0
NRCO | Elk | Inverter | Fan | Repair | Fan - Repair | 1 | Fan failure |  | 02.03 | 1 | Repair | 6/14/2026 | 8:26 pm | 6/14/2026 | 8:46 pm | 154574905 | 630 | Sungrow Inverter Fault Alert
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/14/2026 | 10:10 pm | 6/14/2026 | 10:51 pm | 154718988 | 551 | Power Meter Check 2.0
NRCO | Whitehall | Site | Recloser | Reclosed | Recloser - Reclosed | 1 | SEL Relay is open |  |  | 1 | Outage | 6/14/2026 | 10:21 pm | 6/14/2026 | 10:25 pm | 154813567 | 604 | SEL Recloser Open Alarm
NRCO | Whitehall | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 2 | 1 | Outage | 6/14/2026 | 10:21 pm | 6/14/2026 | 10:27 pm | 154813787 | 630 | Sungrow Inverter Fault Alert
NRCO | Whitetail | Site | Recloser | Reclosed | Recloser - Reclosed | 1 | Recloser Open Register 'Breaker Status': (0 = 0). |  |  | 1 | Outage | 6/14/2026 | 10:37 pm | 6/15/2026 | 4:39 pm | 154815713 | 443 | Data Comparison Alert
NRCO | Whitetail | Site | Recloser | Reclosed | Recloser - Reclosed | 1 | SEL Relay is open |  |  | 1 | Outage | 6/14/2026 | 10:37 pm | 6/15/2026 | 4:21 pm | 154815706 | 604 | SEL Recloser Open Alarm
NRCO | Whitetail | DAS |  |  |  | 0 | Battery Mode Activated |  |  | 1 | Repair | 6/14/2026 | 10:37 pm | 6/15/2026 | 4:21 pm | 154815646 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Whitetail | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 20 | 1 | Outage | 6/14/2026 | 10:37 pm | 6/15/2026 | 12:46 am | 154815420 | 630 | Sungrow Inverter Fault Alert
NRCO | Whitetail | Tracker | TCU | Communication | TCU - Communication | 1 | System Alarm:No AC power detected |  |  | 1 | Repair | 6/14/2026 | 10:44 pm | 6/15/2026 | 4:22 pm | 154816112 | 863 | Gamechange Tracker Alert
NRCO | Washington | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/14/2026 | 10:59 pm | 6/14/2026 | 11:34 pm | 154798001 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/14/2026 | 11:53 pm | 6/15/2026 | 12:38 am | 154821366 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/15/2026 | 12:05 am | 6/15/2026 | 1:08 am | 154822311 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Power phase error |  |  | 1 | Repair | 6/15/2026 | 7:51 am | 6/15/2026 | 10:12 am | 154841183 | 551 | Power Meter Check 2.0
Solential | Graham | Inverter |  | Repair | Repair | 1 | Low voltage 1 (LV1) Phase lock loop failure |  | 9 | 1 | Repair | 6/15/2026 | 11:21 am | 6/16/2026 | 1:30 am | 154854004 | 2899 | Solectria XGI 1500 Series - Fault Alert
NRCO | Whitehall | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/15/2026 | 12:31 pm | 6/16/2026 | 12:23 am | 154859426 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Williams | Tracker | Motor | Stuck | Motor - Stuck | 1 | TCU Fault58: State of charge is not enough to reach target position in a safe way |  | 58 | 1 | Repair | 6/15/2026 | 12:34 pm | 6/15/2026 | 12:44 pm | 154860467 | 3635 | Solar FlexRack/OMCO Tracker Alert (revM)
NRCO | Harding | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/15/2026 | 1:23 pm | 6/16/2026 | 12:45 am | 154864945 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Whitetail | Tracker | TCU | Communication | TCU - Communication | 1 | Individual Tracker Alarm92: No Communication Individual Tracker Alarm93: No Communication |  | 92-93 | 2 | Repair | 6/15/2026 | 4:44 pm | 6/15/2026 | 5:04 pm | 154887872 | 863 | Gamechange Tracker Alert
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/15/2026 | 10:32 pm | 6/15/2026 | 10:57 pm | 154844176 | 551 | Power Meter Check 2.0
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/15/2026 | 11:24 pm | 6/16/2026 | 12:07 am | 154844241 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/15/2026 | 11:57 pm | 6/16/2026 | 12:06 am | 154929599 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/16/2026 | 12:05 am | 6/16/2026 | 1:08 am | 154929291 | 551 | Power Meter Check 2.0
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Power phase error/Alerts are too sensitive and happening during the night. Low irradiance in the area is also effecting these alerts. |  |  | 1 | Repair | 6/16/2026 | 12:21 am | 6/16/2026 | 12:43 am | 154930822 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/16/2026 | 12:41 am | 6/16/2026 | 1:06 am | 154932315 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/16/2026 | 10:59 am | 6/16/2026 | 11:21 am | 154958851 | 551 | Power Meter Check 2.0
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/16/2026 | 11:14 pm | 6/16/2026 | 11:49 pm | 154957338 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/16/2026 | 11:20 pm | 6/16/2026 | 11:46 pm | 155038549 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/17/2026 | 12:18 am | 6/17/2026 | 1:05 am | 155040444 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/17/2026 | 12:34 am | 6/17/2026 | 1:00 am | 155042614 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | Tracker | TCU | Battery Low | TCU - Battery Low | 1 | Slave Alarms S 25: State Of Charge is under the critical threshold Slave Alarms S 94: State Of Charge is under the critical threshold |  | 25, 94 | 2 | Repair | 6/17/2026 | 3:13 am | 6/17/2026 | 12:37 pm | 155052623 | 974 | Solar FlexRack Tracker Alert (revG)
All Bright | Monroe | Inverter | DC Wire | Repair | DC Wire - Repair | 1 | Insulation Resistance Low - IsolationErr |  |  | 1 | Repair | 6/17/2026 | 10:31 am | 6/18/2026 | 9:32 am | 155068083 | 438 | .Chint / Solectria / Canadian String Inv Faults
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/17/2026 | 10:36 am | 6/17/2026 | 11:05 am | 155044387 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/17/2026 | 11:10 am | 6/17/2026 | 11:14 am | 155071213 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | Tracker | TCU | Battery Low | TCU - Battery Low | 1 | Slave Alarms S 54: Emergency stop button pressed Slave Alarms S 6: State Of Charge is under the critical threshold |  | 6, 54 | 2 | Repair | 6/17/2026 | 11:50 am | 6/18/2026 | 3:58 am | 155074724 | 974 | Solar FlexRack Tracker Alert (revG)
NRCO | Shorthorn | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 8 | 1 | Outage | 6/17/2026 | 1:32 pm | 6/17/2026 | 1:42 pm | 155085506 | 630 | Sungrow Inverter Fault Alert
TMI | GSR-Rio | DAS | Weather station |  | Weather station | 0 | Mid day module temperature low module 1: 23.4 °C |  | 1 | 1 | Repair | 6/17/2026 | 2:02 pm | 6/17/2026 | 3:09 pm | 154874846 | 499 | Weather Station Alert
NRCO | Whitetail | Tracker | TCU | Communication | TCU - Communication | 1 | Individual Tracker Alarm155: No Communication |  | 155 | 1 | Repair | 6/17/2026 | 2:08 pm | 6/17/2026 | 2:46 pm | 155090814 | 863 | Gamechange Tracker Alert
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/17/2026 | 10:21 pm | 6/17/2026 | 10:42 pm | 155040511 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/18/2026 | 12:00 am | 6/18/2026 | 12:37 am | 155155277 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | Tracker | TCU | Battery Low | TCU - Battery Low | 1 | Slave Alarms S 54: Emergency stop button pressed Slave Alarms S 48: State Of Charge is under the critical threshold |  | 48, 54 | 2 | Repair | 6/18/2026 | 4:02 am | 6/18/2026 | 12:17 pm | 155168475 | 974 | Solar FlexRack Tracker Alert (revG)
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Power phase error |  |  | 1 | Repair | 6/18/2026 | 9:43 am | 6/18/2026 | 10:04 am | 155156793 | 551 | Power Meter Check 2.0
NRCO | Whitetail | Tracker | TCU | Communication | TCU - Communication | 1 | Individual Tracker Alarm137: No Communication ¦ Individual Tracker Alarm152: No Communication |  | 137, 152 | 2 | Repair | 6/18/2026 | 10:36 am | 6/18/2026 | 5:10 pm | 155181089 | 863 | Gamechange Tracker Alert
NRCO | Shorthorn | Tracker | TCU | Communication | TCU - Communication | 1 | Slave Alarms S 25: System Monitor has detected an out of range or fault condition (check system monitor status) |  | 25 | 1 | Repair | 6/18/2026 | 10:51 am | 6/18/2026 | 7:47 pm | 155152316 | 974 | Solar FlexRack Tracker Alert (revG)
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Power phase error ¦ Current mismatch |  |  | 2 | Repair | 6/18/2026 | 11:46 am | 6/18/2026 | 12:49 pm | 155155514 | 551 | Power Meter Check 2.0
NRCO | Whitetail | Tracker | TCU | Stow | TCU - Stow | 1 | Individual Tracker Alarm137: Low battery stow |  | 137 | 1 | Repair | 6/18/2026 | 1:04 pm | 6/18/2026 | 2:08 pm | 155193902 | 863 | Gamechange Tracker Alert
NRCO | Williams | DAS | Weather station |  | Weather station | 0 | Invalid ambient temperature (TempF) Invalid module 1 temperature (Temp1) |  |  | 1 | Repair | 6/18/2026 | 2:59 pm | 6/18/2026 | 3:00 pm | 155206764 | 499 | Weather Station Alert
Solential | Graham | Inverter |  | Repair | Repair | 1 | Internal communication 1 failure |  | 11 | 1 | Repair | 6/18/2026 | 5:42 pm | 6/18/2026 | 5:43 pm | 155226516 | 2899 | Solectria XGI 1500 Series - Fault Alert
NRCO | Washington | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/18/2026 | 9:41 pm | 6/18/2026 | 10:42 pm | 154820446 | 551 | Power Meter Check 2.0
NRCO | Sunflower | Site | Recloser | Reclosed | Recloser - Reclosed | 1 | SEL Relay is open |  |  | 1 | Outage | 6/18/2026 | 10:17 pm | 6/19/2026 | 11:23 am | 155259640 | 604 | SEL Recloser Open Alarm
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/18/2026 | 10:34 pm | 6/18/2026 | 10:42 pm | 155261175 | 551 | Power Meter Check 2.0
NRCO | Sunflower | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 34 | 1 | Outage | 6/18/2026 | 10:48 pm | 6/19/2026 | 12:34 am | 155262714 | 630 | Sungrow Inverter Fault Alert
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/18/2026 | 11:25 pm | 6/18/2026 | 11:50 pm | 155244536 | 551 | Power Meter Check 2.0
NRCO | Upson | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 7 | 1 | Outage | 6/18/2026 | 11:30 pm | 6/18/2026 | 11:31 pm | 155266086 | 630 | Sungrow Inverter Fault Alert
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/19/2026 | 12:18 am | 6/19/2026 | 1:12 am | 155265042 | 551 | Power Meter Check 2.0
NRCO | Williams | Site | Recloser | Reclosed | Recloser - Reclosed | 1 | SEL Relay is open |  |  | 1 | Outage | 6/19/2026 | 12:45 am | 6/19/2026 | 11:20 am | 155271585 | 604 | SEL Recloser Open Alarm
NRCO | Williams | DAS |  |  |  | 0 | Battery Mode Activated |  |  | 1 | Repair | 6/19/2026 | 1:04 am | 6/19/2026 | 1:06 am | 155272898 | 3618 | Phoenix Contact - Quint UPS Alerts (QUINT4 EIP)
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/19/2026 | 10:57 am | 6/19/2026 | 11:39 am | 155289682 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/19/2026 | 11:27 am | 6/19/2026 | 11:32 am | 155297740 | 551 | Power Meter Check 2.0
NRCO | Elk | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 03.08 | 1 | Outage | 6/19/2026 | 11:33 am | 6/20/2026 | 12:50 am | 155298420 | 630 | Sungrow Inverter Fault Alert
NRCO | Longleaf | Inverter | DC Wire | Repair | DC Wire - Repair | 1 | System low insulation resistance |  | A10 | 1 | Repair | 6/19/2026 | 11:38 am | 6/19/2026 | 11:48 am | 155298730 | 630 | Sungrow Inverter Fault Alert
Solential | Graham | Inverter |  | Fault | Fault | 1 | Low voltage 1 (LV1) Open phase detected ¦ Low voltage 1 (LV1) Open phase detected [3:10 pm] |  | 9 | 1 | Repair | 6/19/2026 | 3:10 pm | 6/20/2026 | 1:35 am | 155319522 | 2899 | Solectria XGI 1500 Series - Fault Alert
TMI | GSR-Gallia | Inverter | Fan | Repair | Fan - Repair | 1 | External Fan Err - ExtFanerr |  |  | 1 | Repair | 6/19/2026 | 4:42 pm | 6/19/2026 | 5:05 pm | 148587595 | 438 | .Chint / Solectria / Canadian String Inv Faults
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/19/2026 | 5:43 pm | 6/19/2026 | 6:24 pm | 155271597 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Weather station |  | Weather station | 0 | Mid day module temperature low module 1: 26.7 °C |  | 1 | 1 | Repair | 6/19/2026 | 5:58 pm | 6/20/2026 | 2:35 pm | 155110427 | 499 | Weather Station Alert
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/19/2026 | 11:19 pm | 6/20/2026 | 12:30 am | 155269778 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | Tracker | TCU | Battery Low | TCU - Battery Low | 1 | Slave Alarms S 25: State Of Charge is under the critical threshold |  | 25 | 1 | Repair | 6/19/2026 | 11:25 pm | 6/20/2026 | 6:45 am | 155371244 | 974 | Solar FlexRack Tracker Alert (revG)
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/20/2026 | 12:15 am | 6/20/2026 | 12:38 am | 155374445 | 551 | Power Meter Check 2.0
Konisto | Marble | Inverter |  | Fault | Fault | 1 | Inverter Faults Detected |  | 1 | 1 | Repair | 6/20/2026 | 4:43 am | 6/20/2026 | 12:36 pm | 155387737 | 2750 | Sungrow 3150U/3425U/3600U inverter alerts
NRCO | Bulloch2 | Inverter | DC Wire | Repair | DC Wire - Repair | 1 | System low insulation resistance |  | 24 | 1 | Repair | 6/20/2026 | 11:03 am | 6/20/2026 | 11:08 am | 155401021 | 630 | Sungrow Inverter Fault Alert
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/20/2026 | 11:06 am | 6/20/2026 | 11:49 am | 155396152 | 551 | Power Meter Check 2.0
TMI | Eagle | Inverter | Fan | Repair | Fan - Repair | 1 | External Fan Err - ExtFanerr |  | 8 | 1 | Repair | 6/20/2026 | 1:52 pm | 6/21/2026 | 9:29 am | 155415717 | 438 | .Chint / Solectria / Canadian String Inv Faults
NRCO | Sunflower | Xfmr |  | Repair | Repair | 1 | 90 degree liquid temp fault - Temperature greater than 90 C. 105 degree liquid temp fault - Temperature greater than 105 C |  | IO0 | 1 | Repair | 6/20/2026 | 6:01 pm | 6/21/2026 | 2:29 am | 155442571 | 534 | Transformer Monitor
NRCO | Washington | Site | Recloser | Reclosed | Recloser - Reclosed | 1 | SEL Relay is open |  |  | 1 | Outage | 6/20/2026 | 6:40 pm | 6/20/2026 | 6:42 pm | 155446761 | 604 | SEL Recloser Open Alarm
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/20/2026 | 11:04 pm | 6/21/2026 | 12:55 am | 155375688 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/20/2026 | 11:36 pm | 6/20/2026 | 11:44 pm | 155473616 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/21/2026 | 12:18 am | 6/21/2026 | 12:58 am | 155475517 | 551 | Power Meter Check 2.0
NRCO | Washington | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/21/2026 | 9:37 pm | 6/21/2026 | 10:05 pm | 155566867 | 548 | Phoenix Contact - Quint UPS Alerts
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/21/2026 | 10:19 pm | 6/22/2026 | 12:10 am | 155538950 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/21/2026 | 10:51 pm | 6/22/2026 | 12:28 am | 155499681 | 551 | Power Meter Check 2.0
All Bright | Monroe | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/21/2026 | 11:02 pm | 6/21/2026 | 11:41 pm | 155405016 | 551 | Power Meter Check 2.0
NRCO | Washington | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/21/2026 | 11:22 pm | 6/22/2026 | 12:00 am | 155263428 | 551 | Power Meter Check 2.0
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/22/2026 | 12:04 am | 6/22/2026 | 12:12 am | 155578221 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/22/2026 | 12:25 am | 6/22/2026 | 12:55 am | 155574478 | 551 | Power Meter Check 2.0
Solential | Graham | Inverter |  | Repair | Repair | 1 | Shutdown Command - AC Switch Low voltage 1 (LV1) |  | 9 | 1 | Repair | 6/22/2026 | 11:24 am | 6/23/2026 | 2:22 pm | 155607163 | 2899 | Solectria XGI 1500 Series - Fault Alert
Miller | RRH | Inverter | Fan | Repair | Fan - Repair | 1 | External Fan Err - ExtFanerr |  | 19 | 1 | Repair | 6/22/2026 | 4:15 pm | 6/22/2026 | 5:14 pm | 155634266 | 438 | .Chint / Solectria / Canadian String Inv Faults
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/22/2026 | 6:50 pm | 6/22/2026 | 7:21 pm | 155650634 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/22/2026 | 8:08 pm | 6/22/2026 | 8:31 pm | 155579593 | 551 | Power Meter Check 2.0
NRCO | Whitetail | Tracker | TCU | Communication | TCU - Communication | 1 | Individual Tracker Alarm233: No Communication |  | 233 | 1 | Repair | 6/22/2026 | 8:22 pm | 6/22/2026 | 8:50 pm | 155661686 | 863 | Gamechange Tracker Alert
Solential | Graham | Inverter |  | Offline | Offline | 1 | Remote Shutdown Command - GUI |  | 24 | 1 | Repair | 6/22/2026 | 8:58 pm | 6/22/2026 | 8:59 pm | 155665271 | 2899 | Solectria XGI 1500 Series - Fault Alert
Konisto | Maple | DAS |  |  |  | 0 | Battery Over Temperature |  |  | 1 | Repair | 6/22/2026 | 10:05 pm | 6/23/2026 | 12:55 am | 155671558 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Washington | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 36 | 1 | Outage | 6/22/2026 | 10:49 pm | 6/23/2026 | 12:43 am | 155675856 | 630 | Sungrow Inverter Fault Alert
TMI | GSR-Rio | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/23/2026 | 12:05 am | 6/23/2026 | 12:49 am | 155672121 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Power phase error/Alerts are too sensitive and happening during the night. Low irradiance in the area is also effecting these alerts. |  |  | 1 | Repair | 6/23/2026 | 12:31 am | 6/23/2026 | 1:08 am | 155675958 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Power phase error |  |  | 1 | Repair | 6/23/2026 | 9:20 am | 6/23/2026 | 9:40 am | 155703254 | 551 | Power Meter Check 2.0
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/23/2026 | 10:51 am | 6/23/2026 | 11:17 am | 155706136 | 551 | Power Meter Check 2.0
TMI | GSR-Rio | DAS | Weather station |  | Weather station | 0 | Mid day module temperature low module 1: 21.7 °C |  | 1 | 1 | Repair | 6/23/2026 | 2:02 pm | 6/23/2026 | 3:02 pm | 155434493 | 499 | Weather Station Alert
NRCO | Mclean | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | 7 | 1 | Outage | 6/23/2026 | 3:30 pm | 6/23/2026 | 3:35 pm | 155741832 | 630 | Sungrow Inverter Fault Alert
TMI | GSR-Rio | DAS | Weather station |  | Weather station | 0 | Mid day module temperature low module 1: 28.0 °C |  | 1 | 1 | Repair | 6/23/2026 | 5:59 pm | 6/24/2026 | 2:21 pm | 155752739 | 499 | Weather Station Alert
NRCO | Gray Fox | DAS |  |  |  | 0 | Battery Voltage Low |  |  | 1 | Repair | 6/23/2026 | 9:19 pm | 6/23/2026 | 9:21 pm | 155778506 | 548 | Phoenix Contact - Quint UPS Alerts
NRCO | Shorthorn | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/23/2026 | 11:55 pm | 6/23/2026 | 11:56 pm | 155791651 | 551 | Power Meter Check 2.0
Miller | RRH | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/24/2026 | 12:43 am | 6/24/2026 | 1:05 am | 155794834 | 551 | Power Meter Check 2.0
NRCO | Warbler | Inverter |  | Tripped Offline | Tripped Offline | 1 | Islanding (Grid power outage) |  | B24 | 1 | Outage | 6/24/2026 | 11:01 am | 6/24/2026 | 12:35 pm | 149492044 | 630 | Sungrow Inverter Fault Alert
TMI | GSR-Gallia | DAS | Production Meter | Troubleshoot | Production Meter - Troubleshoot | 0 | Current mismatch |  |  | 1 | Repair | 6/24/2026 | 11:24 am | 6/24/2026 | 11:46 am | 155795212 | 551 | Power Meter Check 2.0

## Unresolved Alerts
Contractor | Project | Equip | SubPart | Issue4Work | Work | CreateLoss | Comments | Repair (P) | Unit ID | QTY | Bucket | Start Date | Start Time | End Date | End Time | alert_id | event_type_code | event_type_name